22410 | 2025-11-21 | 2025 | 11 | 2025-11 | Leakage | TRUE | high | evaporator coil leak | refrigerant | FALSE | TRUE | Compressor | Low charge | EAHATN-60 | EAHATN | 5 |  | 2023-03-16 | 2025-11-20 | 980 | >2y | Please credit FW Webb Hyannis for a eac1099000009 | Issue 1: Unit shutting off on low charge Diagnosis: System refrigerant recovered Leak Checked. Found Leak in Evaporator |  |  | EAHATN-60 |  |  |  | EAC1099000009
22421 | 2025-11-21 | 2025 | 11 | 2025-11 | Drain Pan | TRUE | medium | faulty drain trap | drain_water | FALSE | TRUE | Other | na | . | . |  |  | 2025-11-21 | 2025-11-21 | 0 | ≤30d (infant) | Faulty drain trap | Faulty drain trap |  | . | . | MGH96M120D5A | . | Other | Drain trap
22448 | 2025-11-24 | 2025 | 11 | 2025-11 | Leakage | TRUE | high | evaporator coil leak | refrigerant | FALSE | TRUE | Other | na | . | . |  |  |  | 2025-11-24 |  | unknown | Coil Leak | Coil Leak |  | . | EAHATN-36BAA | . | . | Evaporator assembly | EAC1099000008
22450 | 2025-11-24 | 2025 | 11 | 2025-11 | APP | TRUE | low | app connection failure | communication | FALSE | FALSE | Other | na | . | . |  |  | 2025-11-24 | 2025-11-24 | 0 | ≤30d (infant) | indoor AH is not registering on ESS PRO APP | indoor AH is not registering on ESS PRO APP |  | . | EAHAEC-36 | . | . |  | na
22452 | 2025-11-24 | 2025 | 11 | 2025-11 | Gas Furnace | TRUE | high | defective control board | control_board | FALSE | TRUE | Other | nL | . | . |  |  |  | 2025-11-24 |  | unknown | nL code. | The conversation focused on troubleshooting an E5 error code related to a gas valve and control board issue. The participants discussed potential causes and solutions for the problem. Recap The caller reported an nL error code related to a gas valve that was ordered 8 days ago, indicating it would not work due to the same error code persisting. Leo Jin suggested checking the control board and confirmed that if the monometer reads 3.2, the gas valve is functioning correctly, and the 24 volts is controlling it. The caller mentioned they were receiving 28 volts across one side of the switch, indicating a potential issue with the low pressure switch, but noted that there was no water in the condensate, ruling out that as a cause. Leo Jin indicated they would add another person to the call for further assistance with the troubleshooting process. Tasks Leo Jin will add another person to the call to assist with troubleshooting the nL error code. |  | . | . | MGH96M060B3A | . | MCB | 17127600000708
22462 | 2025-11-24 | 2025 | 11 | 2025-11 | Valve | TRUE | low | rusted EEV coil | mechanical | FALSE | TRUE | Other | na | EODA18H-4860BAA | EODA18H | 1.5 |  | 2024-10-31 |  |  | unknown | Rusted EEV Coil | Rusted EEV Coil |  | EODA18H-4860BAA | . | . | 167TXWQ500ZQ51200140 |  | EAC3120290034
22472 | 2025-11-25 | 2025 | 11 | 2025-11 | MCB | TRUE | high | condenser PCB failure | control_board | FALSE | TRUE | Control Board | E0 | EODA18H-4860 | EODA18H | 1.5 |  | 2022-10-31 | 2025-11-25 | 1121 | >2y | bad board on outside unit/bad compressor | Anderson (Thomas Kennedy, Plumbing and Heating) reported issues with an E-Core heat pump system that wasn't functioning properly. Mauricio (Technical Support Representative) inquired about the thermostat and the heat pump's condition, confirming it was an older model. Diagnostic checks indicated that the heat pump was displaying an E0 error code, suggesting a bad board in the condenser unit. Anderson mentioned the age of the system, which was over three years old, indicating potential warranty coverage issues. Mauricio explained the need for a surge protector to prevent future failures, stressing that the company would not cover any further damage if it was not installed. Part numbers for a new compressor and board were to be sent to Anderson for ordering and replacement. They discussed the importance of properly installing and configuring the new parts to ensure system functionality. A ticket was created for Anderson, and Mauricio provided his cell number for any future queries. The conversation ended with Mauricio reassuring Anderson of support and guidance in resolving the issue efficiently. They agreed on the next steps for repair. During the conversation, Anderson (Thomas Kennedy, Plumbing and Heating) reported that his E-Core heat pump system was malfunctioning, specifically not activating and having thermostat issues.Mauricio (Technical Support Representative) diagnosed the problem as a likely bad board in the condenser unit after discussing the error code E0. They also confirmed the unit was over three years old, which affected warranty coverage.Mauricio stressed the need for a surge protector to prevent future damage and provided part numbers for ordering a new compressor and board. A ticket was created for Anderson, and Mauricio offered his cell number for further assistance, ensuring a supportive follow-up as they outlined the necessary steps to resolve the heating issues. |  | EODA18H-4860 | EAHATN-60 | n a | 1O608WL800ZL81600664 | MCB | EAC230904171/EAC231235532
22474 | 2025-11-25 | 2025 | 11 | 2025-11 | E-code | TRUE | medium | condenser pipe thermistor failure | refrigerant | FALSE | TRUE | Sensor | F2 | EODA18H-2436 | EODA18H | 1.5 |  | 2020-06-23 | 2025-11-25 | 1981 | >2y | F2 error | F2 error |  | EODA18H-2436 | . | . | 11649WJ4290J60100063 | Other | 230901233
22475 | 2025-11-25 | 2025 | 11 | 2025-11 | MCB | TRUE | high | faulty main control board | control_board | FALSE | TRUE | Other | Blank display | EODA18H-4860 | EODA18H | 1.5 |  | 2022-11-16 |  |  | unknown | BLANK SCREEN ON THE BOARD (1of3) | BLANK SCREEN ON THE BOARD |  | EODA18H-4860 | . | . | 1W967WM400ZM40100311 | MCB | EAC230904171
22476 | 2025-11-25 | 2025 | 11 | 2025-11 | MCB | TRUE | high | faulty main control board | control_board | FALSE | TRUE | Other | Blank display | EODA18H-4860 | EODA18H | 1.5 |  | 2022-11-16 |  |  | unknown | BLANK SCREEN ON THE BOARD (2of3) | BLANK SCREEN ON THE BOARD |  | EODA18H-4860 | . | . | 1W967WM300ZM32200180 | MCB | EAC230904171
22477 | 2025-11-25 | 2025 | 11 | 2025-11 | MCB | TRUE | high | faulty main control board | control_board | FALSE | TRUE | Other | Blank display | EODA18H-4860 | EODA18H | 1.5 |  | 2022-11-16 |  |  | unknown | BLANK SCREEN ON THE BOARD (3of3) | BLANK SCREEN ON THE BOARD |  | EODA18H-4860 | . | . | 1W967WM400ZM40100375 | MCB | EAC230904171
22480 | 2025-11-25 | 2025 | 11 | 2025-11 | Drain Pan | TRUE | medium | cracked drain pan | drain_water | FALSE | TRUE | Other | na | na | NA | [5 empty] | unknown | craked drain pan | The caller requested a replacement for a cracked drain pan on an Eco air handler, providing the model number as EAH-ATN-48. Mauricio Cordeiro confirmed the model number and inquired about the presence of a Gateway outside the unit, which the caller confirmed was not available. Tasks Mauricio Cordeiro will look up the replacement part for the Eco air handler model EAH-ATN-48. |  | na | EAHTN-48 | na | na |  | 23071415
22485 | 2025-11-25 | 2025 | 11 | 2025-11 | Leakage | TRUE | medium | evaporator coil leak | refrigerant | FALSE | TRUE | Other | na | na | NA |  |  |  | 2025-11-25 |  | unknown | coil leak | The technician, Bob from GNC Plumbing and Heating, reported a heating issue with a TN-36 unit, indicating low refrigerant and oil presence in the evaporator pan. They sought to confirm if the unit was under warranty. Mauricio confirmed that the unit is likely under a 10-year warranty and assured Bob that the warranty is not affected by changes in ownership of the house. Mauricio provided Bob with a part number (EAC 10 111 111 5) to order from their supply house, FW Webb, and agreed to create a ticket for warranty processing. Mauricio requested Bob to send pictures of the oil leak for documentation purposes and promised to text him the part number and ticket number after the call. Tasks Mauricio will text Bob the part number and ticket number for warranty processing. Bob will send pictures of the oil leak to Mauricio for documentation. |  | na | EAHTN-36 | na | na | Evaporator assembly | EAC1099000008
22486 | 2025-11-25 | 2025 | 11 | 2025-11 | MCB | TRUE | high | defective eev coil board | control_board | FALSE | TRUE | Refrigerant Circuit | C2 | EODA18H-4860BAA | EODA18H | 1.5 |  |  | 2025-11-24 |  | unknown | bad boars and bad EEv coil | site visit .found bad coil on eev and after replacing it found error code C2 replaced board and unit run ok |  | EODA18H-4860BAA | na | na | 167TXWQ500ZQ51200026 |  | EAC230904171
22488 | 2025-11-25 | 2025 | 11 | 2025-11 | MCB | TRUE | high | blower motor failure | mechanical | FALSE | TRUE | Other | na | na | NA |  |  |  | 2025-11-25 |  | unknown | bad motor and circuit board | Mauricio confirmed the Gateway serial number as 101747 and noted that the unit was previously installed on 07/24/2020. Neil provided the address for the customer as 106 Ridge Crest Drive, Waxahachie, Texas, and explained that the blower motor was intermittently working. Mauricio identified the required parts: the motor with part number 230904170 and the control board with part number 2309044221. Mauricio agreed to create a ticket for warranty purposes and to send Neil a text message with the part numbers and a request for Neil's company information for shipping. Neil confirmed that he would send a picture of his invoice to provide his company details, facilitating the parts order. Tasks Mauricio will send Neil a text message with the part numbers for the motor and control board. Neil will send Mauricio a picture of his invoice containing his company information for shipping purposes. Mauricio will create a ticket number for warranty records and follow up with Leo in Plano, Texas, to ensure the parts are sent to Neil's shop. |  | na | EAHATN -48 | na | na |  | 230904170/230904221
22491 | 2025-11-25 | 2025 | 11 | 2025-11 | Leakage | TRUE | high | leaking evaporator coil | refrigerant | FALSE | TRUE | Other | No refrigerant | EAHATN-60BAA | EAHATN | 5 |  |  | 2025-11-24 |  | unknown | Leaking coil please credit Webb Hyannis | Issue 1: Unit shutting off on low charge Diagnosis: System refrigerant recovered Leak Checked. Found Leak in Evaporator |  |  | EAHATN-60BAA |  |  | None;Evaporator assembly | EAC1099000009
22492 | 2025-11-25 | 2025 | 11 | 2025-11 | MCB | TRUE | high | main control board failure | control_board | FALSE | TRUE | Refrigerant Circuit | C0 | EODA18H-2436 | EODA18H | 1.5 |  |  | 2025-11-25 |  | unknown | E0 Error | E0 Error |  | EODA18H-2436 | . | . | 1W123WM100ZM11600124 | MCB | EAC230904173
22536 | 2025-11-28 | 2025 | 11 | 2025-11 | Drain Pan | TRUE | medium | condensate collector box leak | drain_water | FALSE | TRUE | Other | na | na | NA |  |  |  | 2025-11-26 |  | unknown | water leak at condensation drain cover | Tech Support from Village Home Services reported a leak from the condensate collector box of an ecoer furnace and requested assistance in finding the part number. Mauricio confirmed the part number as EAC 121276 and stated that the part is in stock. Mauricio advised that the part should come with a gasket and suggested using high-temperature silicone as an alternative sealant if needed. Tech Support confirmed their supplier is the Portland group, and Mauricio explained that the part would be shipped from Texas, including the gasket, as it is a new unit. Mauricio recommended that Tech Support create a ticket for warranty purposes to ensure reimbursement for the part when the old one is returned. Tech Support provided their name, Craig, and company name, Village Home Services, along with their main location in Chelmsford, Massachusetts, and the serial number of the unit for ticket creation. Mauricio committed to texting Tech Support the part number and ticket number for record-keeping and requested pictures of the cracked part for future reference during meetings with engineers. Tasks Mauricio will text Tech Support the part number EAC 121276 and the ticket number for record-keeping. Tech Support is to take pictures of the cracked part before replacement and call Mauricio directly for further assistance. |  | na | na | MGH96M100C5A | na |  | EAC12127600000019
22537 | 2025-11-28 | 2025 | 11 | 2025-11 | MCB | TRUE | high | power supply issue at board | electrical | FALSE | TRUE | Other | na | EODA18H-2436 | EODA18H | 1.5 |  |  | 2025-11-26 |  | unknown | bad board on condenser | Mauricio Cordeiro confirmed the model number of the condenser and discussed the issue with the old board, which did not turn on the condenser, resulting in no LED display lights. They identified that the new board was flickering and advised Ethan to check the voltage going into the board, suggesting a possible power issue. Mauricio emphasized the importance of contacting them before replacing parts under warranty to avoid unnecessary costs, as boards are expensive. They discussed the need for Ethan to send a picture of the surge protector to confirm its status, which Ethan agreed to do. Mauricio guided Ethan through checking the voltage and continuity of the compressor wires, confirming that the readings were normal. They discussed the installation instructions for the new board, ensuring that Ethan followed the correct procedures, including adjusting a dip switch on the board. Mauricio instructed Ethan on how to navigate the system settings to confirm the board's configuration and troubleshoot further, including checking error codes and compressor speeds. They identified a potential issue with the EMI filter, which was making noise, and Mauricio requested a video of the sound for documentation purposes. Mauricio explained the importance of registering the new gateway for monitoring and discussed the implications of the monitoring contract expiring after three years, advising Ethan on how to re-register the gateway. Tasks Ethan is to send a picture of the surge protector to Mauricio. Ethan is to create a video of the EMI filter noise and send it to Mauricio for documentation. Ethan is to return the old board to Kyle at the Portland Group, ensuring Mauricio's name is on it for tracking purposes. Ethan is to register the new gateway in the app to ensure it is online. |  | EODA18H-2436 | na | na | 1A521WM700ZM71402132 | MCB | EAC230904173
22539 | 2025-11-28 | 2025 | 11 | 2025-11 | MCB | TRUE | high | air handler control board failure | control_board | FALSE | TRUE | Other | na | na | NA |  |  |  | 2025-11-25 |  | unknown | bad board on Air Handler | Colin called to order a control board for a heating unit, which was previously identified as having a bad control board. Mauricio confirmed the need for a warranty ticket number to proceed with the order. The model number of the unit was confirmed as EAHATN-36, and the part number for the control board was provided as 230-90-4221. Mauricio assured Colin that he would create a warranty ticket and send a text message with the part number for Colin's records to avoid any future errors in ordering the part. Colin confirmed that the warranty would be processed through the Bridgewater location, and Mauricio agreed to send the necessary information shortly. Tasks Mauricio will create a warranty ticket for the control board order. Mauricio will send Colin a text message with the part number and ticket number for record-keeping. |  | na | EAHATN-36 | na | na | AHU Motherboard;Blower Motor | 230904221 / 230904148 (01/23/26)
22541 | 2025-11-28 | 2025 | 11 | 2025-11 | BAD ODU | TRUE | high | rusted EEV coil | mechanical | FALSE | TRUE | Refrigerant Circuit | C2 | EODA18H-4860BAA | EODA18H | 1.5 |  | 2024-10-01 | 2025-11-24 | 419 | 1-2y | system going on low pressure. Coil at EEV all rusted also replaced the board due to C2 error code | Site visit at 4 Algonquin st, Buzzard bay, Massachusetts 02532 found EEV coil all rusted provided one from unit for parts .tested system after and low pressure went normal .gateway number22486 Mario (Customer) mentioned a problem with a machine in Cape Cod that is not heating. Mauricio (Technical Support Representative) acknowledged the issue and offered assistance. Mario discussed plans to purchase a gateway to troubleshoot the machines remotely. Mauricio explained the functionality of the gateway and its importance for monitoring. Mario confirmed he would send details about the machine to Mauricio for further analysis. They discussed the logistics of the upcoming service visit to Cape Cod. Mario expressed gratitude for Mauricio's help and support. |  | EODA18H-4860BAA | EAHATN-48 | na | 167TXWQ500ZQ51200026 | MCB | EAC230904171
22584 | 2025-12-02 | 2025 | 12 | 2025-12 | MCB | TRUE | high | inverter board C4 fault | control_board | FALSE | TRUE | Refrigerant Circuit | C4 | EODA18H-2436 | EODA18H | 1.5 |  |  | 2025-10-10 |  | unknown | Please credit FW Webb Hyannis for 230904173 | Fault Code: C4 Zero Speed Fault Replaced main control board. Please send credit to Paul Gens Webb Hyannis paul.gens@fwwebb.com 774-414-0447 |  | EODA18H-2436 |  |  | 1A521WM700ZM71402077 | MCB | EAC230904173
22592 | 2025-12-02 | 2025 | 12 | 2025-12 | Leakage | TRUE | high | leaking indoor coil | refrigerant | FALSE | TRUE | Compressor | low ref | EAHATN-60 | EAHATN | 5 |  | 2023-03-15 | 2025-11-28 | 989 | >2y | Please take eac1099000009 out of Morley stock | Contractor called to home because of no heat. System had no refrigerant. Leaking indoor coil. They will be grabbing a replacement from us at Morley. Please take one out of stock. |  |  | EAHATN-60 |  |  | Evaporator assembly | eac1099000009
22605 | 2025-12-02 | 2025 | 12 | 2025-12 | IoT | TRUE | medium | IoT gateway offline | communication | FALSE | FALSE | Refrigerant Circuit | c3 | . | . |  |  | 2022-11-28 | 2012-02-25 |  | unknown | 3 of 5 gateways are not Online | Got in contact with the building manager, the building manager will get the contractor out for further evaluation. | C3 | . | . | . | . |  | na
22609 | 2025-12-03 | 2025 | 12 | 2025-12 | Leakage | TRUE | high | rusted evaporator coil | refrigerant | FALSE | TRUE | Compressor | low ref | EAHATN-60 | EAHATN | 5 |  | 2021-03-01 | 2025-12-02 | 1737 | >2y | Please take a EAC1099000009 | Contractor spoke with Josh Nolan from FW Webb in Springfield. Coil is rusted out and leaking. FW Webb called here asking about a replacement. They are going to send the customer here to pick up a replacement EAC1099000009. Please take it out of our stock. |  |  | EAHATN-60 | . |  | Evaporator assembly | eac1099000009
22622 | 2025-12-03 | 2025 | 12 | 2025-12 | MCB | TRUE | high | faulty outdoor PCB | control_board | FALSE | TRUE | Control Board | E0 | EODA18H-2436 | EODA18H | 1.5 |  | 2025-07-01 |  |  | unknown | bad board error code E0 | The conversation between Mauricio Cordeiro and Jeff focused on diagnosing an issue with an outdoor unit displaying an EO error code. They successfully identified the problem and discussed necessary steps for troubleshooting. Recap Mauricio and Jeff confirmed that the outdoor unit was displaying an EO error code and that it did not have a Gateway. Jeff provided the voltage reading of 245 volts coming into the unit, which Mauricio instructed him to check before and after the EMI board. They discussed the need for Jeff to shut down the power to the unit and confirmed that the board was blinking, indicating it was powered down. Mauricio requested Jeff to take a picture of the surge protector for records, emphasizing its importance for future installations. They identified the compressor wires and discussed the procedure for checking the ohms between the wires, with Mauricio guiding Jeff through the process of using his meter correctly. Tasks Jeff is to take a picture of the surge protector and send it to Mauricio for records. Jeff is to ensure that the new units are installed with a surge protector as per the paperwork. |  | EODA18H-2436 | na | na | 1W123WM100ZM11600175 | MCB | EASC230904173
22624 | 2025-12-03 | 2025 | 12 | 2025-12 | Motor | TRUE | high | failed fan motor blades | mechanical | FALSE | TRUE | Other | na | EODA18H4860 | EODA18H | 1.5 |  |  | 2012-03-25 |  | unknown | bad fan motor and blades on two different condensers | two condensers installed over the summer both need blades and fan motors ,one needs the metal cover .please ship to contractors address. |  | EODA18H4860 | na | na | F52310000100H9150035/1G261WL100ZL12800192 | Choose the part that is needed. | EAC230801635/EAC2323100001 / EAC230801635 / EAC2323100001 / EAC230803291
22654 | 2025-12-04 | 2025 | 12 | 2025-12 | Gas Furnace | TRUE | medium | condensation trap failure | drain_water | FALSE | TRUE | Control Board | E1 | na | NA | [5 empty] | unknown | Furnace going on E1 error code .Trap not working properly | Assisted Leo with this call .Condensation trap not working properly .will be meeting with contractor on 12/05/2025.to see it on the jobsite . |  | na | na | MGH96M100C5A | na |  | na
22663 | 2025-12-05 | 2025 | 12 | 2025-12 | Leakage | TRUE | high | evaporator coil leak | refrigerant | FALSE | TRUE | Other | na | . | . |  |  |  | 2025-10-27 |  | unknown | Coil Leak | Coil leak |  | . | EAHATN-48 | . | . | Evaporator Only | EAC1099000009
22669 | 2025-12-05 | 2025 | 12 | 2025-12 | MCB | TRUE | high | main board failure | control_board | FALSE | TRUE | Other | No display | EODA18H-4860BAA | EODA18H | 1.5 |  | 2025-05-29 | 2025-12-03 | 188 | 31-365d | Please take EAC230904171 out of Morley inventory | Issue 1: Outdoor Heat pump will not start . : No Display on Main Control Board Diagnosis Checked incoming voltage 237 volts Recommendation: Replace Board |  | EODA18H-4860BAA |  |  | 14RR9WP400ZP42100010 | None;MCB | EAC230904171
22685 | 2025-12-05 | 2025 | 12 | 2025-12 | MCB | TRUE | high | main control board failure | control_board | FALSE | TRUE | Control Board | E4 | EODA18H-2436 | EODA18H | 1.5 |  | 2025-08-20 | 2025-12-05 | 107 | 31-365d | Bad MCB | The System has a bad Main control board due to an E4 error code |  | EODA18H-2436 | EAHATN-24 | . | 1O372WLA00ZLA0900089 | MCB | 230904156
22687 | 2025-12-06 | 2025 | 12 | 2025-12 | EMI | TRUE | high | faulty EMI filter | electrical | FALSE | TRUE | Other | NONE | EODA18H-4860 | EODA18H | 1.5 |  | 2021-05-14 | 2025-05-28 | 1475 | >2y | Faulty EMI filter. | Faulty EMI filter. |  | EODA18H-4860 | . |  | 16015WK417ZK81500264 | EMi Filter | 230904159
22689 | 2025-12-06 | 2025 | 12 | 2025-12 | Leakage | TRUE | high | evaporator coil leak | refrigerant | FALSE | TRUE | Other | na | EODA18H-4860 | EODA18H | 1.5 |  | 2022-12-09 |  |  | unknown | Coil Leak | Coil Leak waiting for picture of the leak |  | EODA18H-4860 | EAHATN-48 | . | 1O608WL800ZL80700115 | Evaporator Only | EAC1099000009
22690 | 2025-12-06 | 2025 | 12 | 2025-12 | MCB | TRUE | high | main control board failure | control_board | FALSE | TRUE | Control Board | E1 | . | . |  |  | 2025-01-01 |  |  | unknown | E1 Error | E1 Error. Check that the low fire pressure switch is open, not closed. The pressure switch is good. |  | . | . | MGH96M080C4A | . | MCB | 17127600000708
22695 | 2025-12-06 | 2025 | 12 | 2025-12 | Drain Pan | TRUE | medium | cracked condensate traps | drain_water | FALSE | TRUE | Other | na | . | . | [5 empty] | unknown | Crack condensate traps x2 | Crack condensate traps x2 |  | . | . | MGH96M080B3A x2 | . | Other | condensate trap
22724 | 2025-12-08 | 2025 | 12 | 2025-12 | MCB | TRUE | high | improper dual fuel wiring | control_board | TRUE | TRUE | Other | na | EODA18H4860 | EODA18H | 1.5 |  |  | 2025-12-05 |  | unknown | bad board and dual fuel kit needed | The technician, referred to as Tech Support - DONOVAN COLLEEN, reported an issue with an Eco air unit installed in the summer, specifically a lack of power to the W terminal and an H2 error code on the condenser. Mauricio Cordeiro guided the technician through diagnostic steps, confirming the absence of power on the W terminal and discussing the setup of the dual fuel system, including the use of a rib relay instead of a dual fuel kit. After troubleshooting, it was determined that the board likely needed replacement due to conflicting signals and the persistent H2 error code, indicating a malfunction. Mauricio provided a part number for the replacement board (EAC 2330 904171) and suggested acquiring a dual fuel kit to prevent future issues, emphasizing the importance of proper wiring to avoid mixed signals. The technician was advised to disconnect the rib relay and connect the thermostat directly to the furnace to ensure proper operation, which resulted in the furnace running but still displaying a signal error (NL). |  | EODA18H4860 | na | na | 1068WL800ZL80700189 | MCB | EAC230904171
22726 | 2025-12-08 | 2025 | 12 | 2025-12 | MCB | TRUE | high | board and fan motor failure | control_board | FALSE | TRUE | Other | Outdoor Heat pump will not start. Display C1 to C0 | EODA18H-2436 | EODA18H | 1.5 |  | 2020-03-20 | 2025-12-03 | 2084 | >2y | Please credit FW Webb Plymouth for EAC230904165 & EAC230904010 | Issue 1: Outdoor Heat pump will not start. Display C1 to C0 Diagnosis Checked incoming voltage 237 volts Ohm Compressor, 1.0. 0.9, 0.9 Condenser Fan Motor will not run Recommendation: Replace Board Replace Condenser Fan Motor |  | EODA18H-2436 |  |  | 10372WLA00ZLA0900011 |  | 231235530 (12/17/25) EAC230904165 & 2323100001
22744 | 2025-12-09 | 2025 | 12 | 2025-12 | MCB | TRUE | high | burned circuit board | control_board | FALSE | TRUE | unknown |  | EODA18H-2436 | EODA18H | 1.5 |  |  | 2025-12-08 |  | unknown | burned board at outdoor unit | The technician, John from JP Parks Heating and Cooling, reported a service call for a heating unit with no heat, identifying that the circuit board was completely fried with burn marks and a hole in it. Mauricio requested the model number of the unit, which was provided as E0DA18H-2436, and confirmed that John was on-site during the call. Mauricio instructed John to take a picture of the surge protector connected to the unit and to power down the unit by pulling the disconnect. John was guided to test the wires from the compressor, confirming the presence of a red, blue, and white wire, and was instructed to pull those wires out for further testing. John performed resistance tests on the wires, confirming that the readings were appropriate, and then checked for continuity to ensure the compressor was not grounded, which also returned no issues. Mauricio provided John with the name of the supply house, FW Webb, and committed to sending a part number for the replacement board. John was instructed to call FW Webb to request the new board and to read the accompanying instructions to adjust it to the system. Mauricio requested that John send pictures of the unit after he received the part number, which would be used to create a warranty ticket for the replacement board. Tasks John is to take a picture of the surge protector and send it to Mauricio. John is to power down the unit and pull the disconnect as instructed. John is to test the wires from the compressor as directed and report the findings. John is to call FW Webb to request the new circuit board using the part number that Mauricio will send. John is to send pictures of the unit to Mauricio after receiving the part number. Mauricio will create a warranty ticket for the replacement board and send the ticket number to John. |  | EODA18H-2436 | na | na | 1A521WM700ZM71402112 | MCB | EAC230904173
22748 | 2025-12-09 | 2025 | 12 | 2025-12 | Leakage-motor | TRUE | high | leaking coil and bad motor | refrigerant | FALSE | TRUE | Other | na | EAHATN-24 | EAHATN | 2 |  |  | 2025-12-08 |  | unknown | coil leak and bad motor | The technician reported a leak in the evaporator coil of the echo air unit and requested to send pictures for further assistance. Mauricio provided their email address for the technician to send the pictures and details about the unit. The technician confirmed they would send the pictures and information needed to open a ticket for parts under warranty. Mauricio agreed to create a ticket and arrange for shipping the required parts directly to the technician since there were no local supply houses available. Mauricio committed to sending the ticket number and tracking information for the shipment once available. Tasks The technician will send pictures and details about the echo air unit to Mauricio's email. Mauricio will create a ticket for the parts and send the ticket number to the technician. Mauricio will arrange for shipping the required parts directly to the technician. |  |  | EAHATN-24 |  |  | Blower Motor;Evaporator assembly | EAC1099000008/230904147
22760 | 2025-12-10 | 2025 | 12 | 2025-12 | Motor | TRUE | high | fan motor failure | mechanical | FALSE | TRUE | Other | na | EAHATN-36 | EAHATN | 3 |  |  |  |  | unknown | Fan motor failure | Fan motor failure The fan motor is not operating, and all diagnostic tests indicate that it has failed and needs to be replaced. |  |  | EAHATN-36 | . |  | Fan Motor | 230904148
22770 | 2025-12-10 | 2025 | 12 | 2025-12 | Leakage | TRUE | high | evaporator coil leak | refrigerant | FALSE | TRUE | unknown |  | EAHATN-36 | EAHATN | 3 |  |  | 2025-12-09 |  | unknown | LEAKY EVAP COIL | LEAKY EVAP COIL |  |  | EAHATN-36 |  |  | Evaporator assembly | EAC1099000008
22773 | 2025-12-10 | 2025 | 12 | 2025-12 | E-code | TRUE | low | broken top cover | cosmetic | FALSE | TRUE | Protection | PA, E0 | E0DA18H-2436 | E0DA | 1.5 |  |  | 2012-09-25 |  | unknown | Broken Top Cover on Condenser | Broken Top Cover on Condenser | F2 | E0DA18H-2436 | . | . | 1M511WL600ZL62400058 | Other | EAC230904173 (03/23/26). EAC2323100001 (03/06/26), 230801635 , 230803291, 230803110 X4 , 2319100013 x4
22774 | 2025-12-10 | 2025 | 12 | 2025-12 | Gas Furnace | TRUE | high | faulty gas valve | mechanical | FALSE | TRUE | Other | an | . | . |  |  |  | 2012-09-25 |  | unknown | Johnstone is asking for Gas valve via email | Johnstone is asking for Gas valve via email |  | . | . | MGH96M100C5A | . | Gas valve | 17427600001389
22786 | 2025-12-10 | 2025 | 12 | 2025-12 | Noise | TRUE | medium | internal compressor noise | noise_vibration | FALSE | TRUE | Other | na | EODA18H-4860BAA | EODA18H | 1.5 |  | 2024-10-31 | 2025-12-09 | 404 | 1-2y | bad condenser .making noise when running | Mauricio Cordeiro called to troubleshoot an HVAC system issue, specifically regarding a loud noise from the compressor and the performance of the newly installed EEV valve. The technician confirmed that the EEV valve was replaced but the noise persisted, indicating a possible compressor issue. The technician requested the last six digits of the Gateway serial number to access system data, which was provided as 000045. The technician instructed the caller to run the system in heat mode to observe its performance and report back any error codes. The caller reported a C3 error code and a loud noise from the compressor, prompting the technician to request a video of the noise for further analysis. The technician noted that the system had been running without gas, which could have caused damage to the compressor, and advised the caller to document the model and serial numbers for warranty purposes. The technician created a ticket for the issue and requested the caller to send pictures and videos of the system's performance for further evaluation. The technician discussed the wiring setup of the thermostat, indicating that insufficient wiring could be causing operational issues with the heat pump and furnace. Tasks The caller is to send a 5-second video of the compressor noise to Mauricio Cordeiro. The caller is to provide pictures of the model and serial numbers of the HVAC unit for warranty documentation. Mauricio Cordeiro will create a ticket and discuss the situation with their boss regarding the potential replacement of the compressor. |  | EODA18H-4860BAA | GNC4860CPT | na | 167TXWQ500ZQ51200140 |  | na
22789 | 2025-12-10 | 2025 | 12 | 2025-12 | Drain Pan | TRUE | medium | cracked condensate trap | drain_water | FALSE | TRUE | Other | NONE | . | . |  |  | 2023-03-13 | 2025-07-18 | 858 | >2y | Cracked Condensate Trap | Cracked Condensate Trap |  | . | . | MGH96M120D5A | . | Other | 12127600000932
22791 | 2025-12-10 | 2025 | 12 | 2025-12 | MCB | TRUE | high | main PC board failure | control_board | FALSE | TRUE | Control Board | E0 | EODA 18H 2436 | EODA | 1.5 |  | 2024-03-13 | 2025-12-09 | 636 | 1-2y | bad board on outdoor unit | The caller reported a warranty issue regarding a failed PC board in a heat pump system, specifically indicating an error code of e0 and that a new main PC board is needed. Mauricio confirmed the system's age as 2 years, installed in 2023, and identified it as part of the Harvest thermal system. Mauricio advised the caller to ensure a surge protector is installed on the system and requested that their technicians call him directly during future service visits for warranty issues to facilitate troubleshooting. Mauricio provided his cell phone number (571-491-8318) for direct communication and requested the caller to text him all relevant information about the unit, including model and serial numbers, as well as their company details. The caller confirmed they do not have a Gateway device and that the system operates off a thermostat, which Mauricio acknowledged and noted for the warranty process. Mauricio emphasized the importance of reading the installation paperwork for the new board and instructed the caller to ensure their technician contacts him directly for any questions during the installation process. Tasks The caller is to text Mauricio all relevant information about the unit, including model number, serial number, and company details. Mauricio will send a new main PC board to the caller's company. The caller's technicians are to call Mauricio directly before performing any work on the system to facilitate troubleshooting. |  | EODA 18H 2436 | na | na | 10372WL800ZL81900297 | MCB | EAC230904173
22795 | 2025-12-11 | 2025 | 12 | 2025-12 | E-code | TRUE | high | grounded compressor terminal | electrical | FALSE | TRUE | unknown |  | EODA18H-2436 | EODA18H | 1.5 |  |  | 2012-10-25 |  | unknown | E0, C9 | E0, C9 error, grunded compressor. | E0 | EODA18H-2436 |  |  | 16015WK415ZK60300143 | Compressor | 231235530
22799 | 2025-12-11 | 2025 | 12 | 2025-12 | E-code | TRUE | medium | indoor/outdoor communication error | communication | FALSE | FALSE | Sensor | F7 | EODA18H-2436 | EODA18H | 1.5 |  | 2022-04-06 |  |  | unknown | F7 Error | .F7 Error | F7 | EODA18H-2436 | EAHATN-24 | . | F52290000100H9220082 | Other;MCB | EAC231235159, EAC230904165
22815 | 2025-12-11 | 2025 | 12 | 2025-12 | MCB | TRUE | high | inverter board failure | control_board | FALSE | TRUE | Control Board | E0 | EODA18H-2436 | EODA18H | 1.5 |  | 2020-09-11 | 2025-12-08 | 1914 | >2y | bad board on outside unit | The technician confirmed the model number of the heat pump as E0DA18H-D2436 and the last six digits of the gateway serial number as 102593. The technician established that the heat pump was offline and unable to provide error codes, indicating a potential issue with the inverter. The technician guided the caller to check the error code, which was identified as E0, suggesting a need for a new board. The technician confirmed the installation date of the unit as November 11, 2020, and verified the address as 46 Top Belt Spring Road, Concord, MA. The technician created a ticket number for the issue and requested the caller's phone number for follow-up, which was provided as 978-493-1717. The technician discussed potential supply houses for parts, including SG Torrice and Portland Group, and confirmed that the caller would find a supply house nearby. Tasks The technician will create a ticket number for the issue and send it to the caller's phone number. The technician will follow up with the caller regarding the part number needed for the heat pump |  | EODA18H-2436 | na | na | 12673WK252ZK51900006 | MCB | EAC230904165
22816 | 2025-12-12 | 2025 | 12 | 2025-12 | Leakage | TRUE | high | leaking evaporator coil | refrigerant | FALSE | TRUE | Other | na | . | . |  |  |  | 2012-11-25 |  | unknown | Leaky Coil | The conversation involved a contractor, Gabrielle from Shea Hood and Sons, discussing a leaking coil issue with Leo from Ecore. A case number was established for warranty processing, and Gabrielle agreed to send necessary documentation for the claim. Recap Gabrielle reported a leaking coil at an air handler and confirmed the need for a case number to process the warranty claim. Leo confirmed that he would create a ticket for the warranty claim and requested Gabrielle to send all relevant details, including a video and model information. Gabrielle agreed to send the video and additional documentation, including outdoor and indoor images, to support the warranty claim. Tasks Gabrielle will send a video and documentation regarding the leaking coil to Leo. Leo will create a ticket for the warranty claim and provide Gabrielle with the case number. |  | . | EAHATN- 24 | na | . | Evaporator assembly | EAC1099000008
22817 | 2025-12-12 | 2025 | 12 | 2025-12 | MCB | TRUE | high | outdoor PCB failure | control_board | FALSE | TRUE | Protection | PC49 | ESCA16H-36 | ESCA16H | 3 |  |  |  |  | unknown | bad board on outdoor unit per Chris Morley | Mauricio Cordeiro confirmed the caller's compressor model as ESC A 168 Dash 36 and noted the need for a serial number to proceed with the ticket creation. The caller was advised to send a picture of the serial number to facilitate the ticket process. Mauricio explained that reimbursement for the job site hours must be discussed with Chris, who will relay the information to his boss for approval. Mauricio assured the caller that he would investigate the PC 49 error and text them the part number needed for the board replacement. Tasks Mauricio Cordeiro will investigate the PC 49 error and text the caller with the part number for the board. The caller is to send a picture of the serial number to Mauricio for ticket creation. |  | ESCA16H-36 | n a | na | na | MCB | EAC17222000037996/EAC17222000037997
22823 | 2025-12-12 | 2025 | 12 | 2025-12 | Leakage | TRUE | high | indoor coil leak | refrigerant | FALSE | TRUE | Other | na | na | NA | [5 empty] | unknown | coil leak at air handler | Christopher Garcia from Strand Brothers Heating and Cooling requested a PIN number for an indoor coil they condemned, providing the model number EAHATN-36 and serial number 1856NL2000ZL22500036. Mauricio Cordeiro confirmed the company name as Service Experts and created a ticket for the request, agreeing to send a part number. Mauricio provided the part number EAC10990000008 and instructed Christopher to send a 5-second video of the leak for warranty purposes. Christopher agreed to send the video and confirmed they would send it to the cell phone number Mauricio would text them. Tasks Mauricio will text Christopher Garcia the part number EAC10990000008. Christopher Garcia will send a 5-second video of the coil leak to the cell phone number provided by Mauricio. Mauricio will send a ticket number for the warranty in about 20 minutes. |  | na | EAHATN-36 | na | na | Evaporator assembly | EAC1099000008
22824 | 2025-12-12 | 2025 | 12 | 2025-12 | MCB | TRUE | high | outdoor mainboard failure | control_board | FALSE | TRUE | Control Board | E0 | EODA18H-2436 | EODA18H | 1.5 |  |  | 2025-12-11 |  | unknown | bad board at outdoor unit | Mauricio Cordeiro confirmed the issue with the E0 code and the need for a site visit to verify operations, stating that they would not proceed until they spoke with Degree HVAC. The Tech Support representative from Degree HVAC explained that they had already conducted diagnostics and determined a bad board needed replacement, but they were unsure about the warranty process and who would cover the costs. Mauricio advised the Tech Support representative to take pictures of the board and ensure a surge protector was installed to prevent future issues, emphasizing the importance of following proper procedures. Mauricio provided the part number EAC230904173 for the replacement board and instructed the Tech Support representative to communicate this to their office for ordering. Mauricio offered his contact information for further assistance and reiterated the need for a surge protector to be installed with the new board to avoid voltage issues. Tasks Mauricio Cordeiro will provide the part number EAC230904173 to the Tech Support representative for ordering the replacement board. The Tech Support representative will communicate with their office regarding the part number and the need for a surge protector. |  | EODA18H-2436 | na | na | 10372WL800ZL81900297 | MCB | EAC230904173
22837 | 2025-12-12 | 2025 | 12 | 2025-12 | MCB | TRUE | high | EEPROM parameter error | communication | FALSE | TRUE | Control Board | E0 | EODA18H-4860BAA | EODA18H | 1.5 |  |  |  |  | unknown | E0 Error | E0 Error |  | EODA18H-4860BAA | . | . | 167TXWQ500ZQ51200105 | MCB | EAC230904171
22848 | 2025-12-13 | 2025 | 12 | 2025-12 | IoT | TRUE | medium | gateway communication failure | communication | FALSE | TRUE | Sensor | F8 | EODA18H-4860 | EODA18H | 1.5 |  | 2025-03-01 | 2012-12-25 |  | unknown | System Gateway is not working properly. Also trouble with system operation. | System Gateway is not working properly. Also trouble with system operation. |  | EODA18H-4860 | EAHATN-60 | . | F52310000100HB060169 | Other | EAC1099000009 (3/31/26) EG910L,
22863 | 2025-12-15 | 2025 | 12 | 2025-12 | E-code | TRUE | high | EEPROM parameter error | control_board | FALSE | TRUE | Control Board | Eo Error and code 43 | EODA18H-4860 | EODA18H | 1.5 |  | 2023-08-23 | 2012-12-25 |  | unknown | E0 Error and code 43 | Eo Error and code 43 | E0 | EODA18H-4860 | . | . | 1W967WM600ZM60100979 | MCB;Compressor | EAC230904171, 231235532
22872 | 2025-12-15 | 2025 | 12 | 2025-12 | MCB | TRUE | high | main control board failure | control_board | FALSE | TRUE | Control Board | E0 Error | EODA18H-4860 | EODA18H | 1.5 |  | 2022-08-22 | 2025-12-15 | 1211 | >2y | E0 Error | E0 Error |  | EODA18H-4860 | EAHATN-60 | . | 1W967WM400ZM40100358 | MCB | EAC230904171
22880 | 2025-12-16 | 2025 | 12 | 2025-12 | MCB | TRUE | high | low refrigerant pressure | refrigerant | FALSE | FALSE | Protection | P8 | EODA18H 4860 | EODA18H | 1.5 |  |  | 2025-10-12 |  | unknown | bad board on outdoor unit | The technician confirmed that the heat pump was experiencing low suction and discharge pressures, with readings of 38 PSI and 227 PSI initially, and later 67 PSI and 282 PSI after adjustments were made. The technician identified that the system was offline due to exceeding the monitoring limit and confirmed the address of the unit as 529 to find Drive C4, Delaware. The technician guided the caller through checking the display on the outside unit, confirming it was in heating mode and providing instructions to check various pressure readings. The technician diagnosed a P8 error code indicating low compressor voltage protection and instructed the caller to check the incoming voltage, which was found to be 246 volts. The technician advised the caller to power off the unit and check the compressor wiring, guiding them through measuring resistance across various wires to assess the compressor's condition. The technician concluded that the compressor was likely malfunctioning and recommended sending a new control board, asking the caller to provide a picture of the surge protector for records. Tasks The technician will send the caller a part number and ticket number for warranty purposes regarding the new control board. The caller is to send a picture of the surge protector and the model number of the unit to the technician for records. The caller is to contact their supply house, Johnson Supply, to obtain the new control board using the provided part number. |  | EODA18H 4860 | na | na | 11549WJ4280J50800165 | MCB | EAC230904171
22889 | 2025-12-16 | 2025 | 12 | 2025-12 | MCB | TRUE | high | shorted compressor and board | electrical | FALSE | TRUE | Other | na | EODA18H4860 | EODA18H | 1.5 |  | 2023-09-15 | 2025-12-14 | 821 | >2y | bad board and bad compressor | Jonathan, a contractor from Supreme Mechanical, reported that a heat pump is not functioning properly, indicating that there is power but the board is not lighting up. Mauricio confirmed the model number of the heat pump as EODA18H-4860 and inquired about the presence of a Gateway, which Jonathan confirmed is not installed. After discussing the power supply, Jonathan confirmed that the incoming power is good, but the board is not responding, and no burned components were visible. Mauricio instructed Jonathan to turn off the unit and check the compressor wires, specifically the red, white, and blue wires, to ensure the compressor is not faulty. Jonathan performed tests on the compressor and reported inconsistent readings, indicating potential issues with the compressor or the board. Mauricio suggested that Jonathan check the grounding of the compressor and provided further instructions on testing the wires for continuity. After further testing, Jonathan reported that he was not getting any readings from the compressor, leading Mauricio to suspect a bad compressor and board. Mauricio recommended replacing both the compressor and the board, and advised Jonathan to install a surge protector to prevent future issues due to power fluctuations. Jonathan inquired about suppliers for the replacement parts, and Mauricio provided names of distributors, including FW Webb and Portland Group. Jonathan confirmed the heat pump is two years old and agreed to check for installation paperwork to confirm the installation date. Mauricio requested the serial number of the unit to create a service ticket and promised to send Jonathan the part numbers after consulting with his boss. Tasks Jonathan will check for the installation paperwork to confirm the installation date of the heat pump. Mauricio will consult with his boss regarding the replacement of the compressor and board and will send Jonathan the part numbers after the discussion. Jonathan will send Mauricio a picture of the unit's serial number for the service ticket. |  | EODA18H4860 | na | na | 1A681WM600ZM60500245 | MCB;Compressor | EAC230904171/EAC231235532
22899 | 2025-12-16 | 2025 | 12 | 2025-12 | MCB | TRUE | high | recurring board failure | control_board | FALSE | TRUE | Refrigerant Circuit | C1 /E0 | EODA18H-2436BAA | EODA18H | 1.5 |  | 2025-07-18 | 2025-12-16 | 151 | 31-365d | bad board on outdoor unit | Mauricio and Brett discussed the recurring e0 error code on unit 20 2436 baaa, confirming that the unit is currently in front of Brett and experiencing the issue. They verified that the unit has a buck booster and a built-in surge protector, and confirmed the voltage reading of 233. Mauricio requested the last six digits of the unit's serial number to build a case, which Brett provided as 1Z5 105335. They noted that the unit had previously had a board replaced and discussed the history of error codes, including a C3 error related to compressor module protection. Mauricio confirmed that he would create a service ticket for Brett and would contact an engineer in Texas to review the system's history due to the presence of a Gateway. They discussed the need for Brett to retrofit the new board to the old unit and Mauricio provided the part number (230 904173) for the replacement board. Mauricio committed to sending Brett a text message with the part number and ticket number once created, and requested that Brett take pictures of the surge protector and booster for record-keeping purposes. Tasks Mauricio will create a service ticket for Brett regarding the e0 error code and the replacement board. Mauricio will send Brett a text message with the part number (230 904173) and the ticket number once completed. Brett is tasked with taking pictures of the surge protector and booster for record-keeping and sending them to Mauricio. |  | EODA18H-2436BAA | EAHATN-36 | na | 151ANWP900ZP92700471 | MCB | EAC230904273
22900 | 2025-12-16 | 2025 | 12 | 2025-12 | MCB | TRUE | high | EEPROM parameter error | communication | FALSE | TRUE | Control Board | E0 | EODA19H-4860AAA | EODA19H | 4 |  |  | 2025-12-16 |  | unknown | E0 Error | E0 Error |  | EODA19H-4860AAA | . | . | 0EWH004384Z247040011 | MCB | EAC230904171
22903 | 2025-12-16 | 2025 | 12 | 2025-12 | Leakage | TRUE | high | evaporator coil leak | refrigerant | FALSE | TRUE | Compressor | Leak in Coil | EODHA18-2436 | EODHA18 | 1.5 |  | 2022-10-10 | 2012-12-25 |  | unknown | Leak in coil | Leak in coil Ship To: Kelly Casey 22315 Bute Drive Spicewood, Texas 78669 |  | EODHA18-2436 | EAHATN-36 |  | 1N511WL600ZL62400053 | None;Evaporator assembly | EAC1099000008
22914 | 2025-12-17 | 2025 | 12 | 2025-12 | MCB | TRUE | high | burned control board | control_board | FALSE | TRUE | Other | na | EODA18H2436 | EODA18H | 1.5 |  |  | 2025-12-16 |  | unknown | burned out board on outdoor unit | The technician reported that the outdoor condenser unit (model EODA18H-D2436) is down and requires parts due to a burned-out control board with no display. The technician confirmed that the unit is approximately 2 to 2.5 years old and does not have a surge protector installed, which is recommended for protection against voltage issues. Voltage readings were taken, showing 238 volts, and the technician was instructed to check the compressor's grounding to prevent further damage. The technician provided the serial number (1AA521WM300Z290013) for the unit to create a service ticket. A part number (EAC230904173) for the new control board was communicated, and the technician was advised on installation procedures and programming requirements for the new board. The technician was informed that the part is under warranty, but it was recommended to install a surge protector to avoid future issues, as the warranty may not cover subsequent damages if not installed. Tasks The technician, Michael, is to install the new control board and ensure proper programming as instructed. Michael is to send a picture of the installed surge protector and the model number of the unit once completed. A text message with the part number and ticket number will be sent to Michael for reference. |  | EODA18H2436 | na | na | 1A521WM3002ZM32900013 | MCB | EAC230904173
22942 | 2025-12-18 | 2025 | 12 | 2025-12 | MCB | TRUE | high | grounded compressor failure | electrical | FALSE | TRUE | Refrigerant Circuit | C1, E0 | EODA18H-2436 | EODA18H | 1.5 |  | 2020-09-11 | 2025-12-18 | 1924 | >2y | C1, E0, Grounded Compressor. | C1, E0, Grounded Compressor. |  | EODA18H-2436 | . | . | 12673WK252ZK51900006 | Compressor | 231235530
22945 | 2025-12-19 | 2025 | 12 | 2025-12 | MCB | TRUE | high | malfunctioning outdoor MCB | control_board | FALSE | TRUE | Other | none | EODA18H4860 | EODA18H | 1.5 |  |  | 2025-12-14 |  | unknown | bad board on outdoor unit | Mauricio confirmed the caller's issue with a malfunctioning control board in a unit located in Boston, identifying the need for a replacement board and a surge protector to ensure warranty compliance. The caller provided the model number (EOVA18H-4860) and serial number (1W967WM60000ZM60100747) of the unit, which Mauricio noted for ticket creation. Mauricio explained the importance of installing a surge protector to avoid warranty issues, emphasizing that failure to do so could result in significant costs for the customer. Mauricio agreed to send a part number (EAC230904171) for the replacement board and instructed the caller to take pictures of the installed surge protector for warranty documentation. The caller confirmed their understanding of the process and agreed to send the required pictures and information back to Mauricio. Tasks Mauricio will send the part number for the replacement board to the caller. The caller is responsible for installing the surge protector and sending pictures to Mauricio before replacing the control board. The caller will provide the model number and serial number of the unit to Mauricio for ticket creation. |  | EODA18H4860 | na |  | 1W967WM60000ZM60100747 | MCB | EAC230904171
22948 | 2025-12-19 | 2025 | 12 | 2025-12 | Drain Pan | TRUE | medium | drain line backup | drain_water | TRUE | FALSE | Other | na | na | NA |  |  |  | 2025-12-18 |  | unknown | furnace with drain issues .possible will need to do a site visit . | The technician, Farrell Gregory, reported a drain issue with an ecoair gas furnace model H96 MGH 96 M, 080 b3a, where the drain was backing up and causing the pressure switch to cut off. Mauricio Cordeiro confirmed the furnace's orientation and drain setup, noting that the unit was pitched forward as required. They discussed the flue length, which was approximately 20 feet with 390s, and confirmed it was a 2-inch flue. Mauricio requested Farrell to send pictures of the flue and the collector box setup to better understand the issue. Farrell mentioned that the water level in the collector box was rising and had previously hit the pressure switch line, causing it to cut off, but he had not been able to replicate this situation during the call. Tasks Farrell Gregory is to send pictures of the flue and collector box setup to Mauricio Cordeiro for further analysis. Mauricio Cordeiro will review the pictures once received to assist in troubleshooting the furnace issue. |  |  | na | MGH96-M80B3A |  |  | na
22970 | 2025-12-20 | 2025 | 12 | 2025-12 | MCB | TRUE | high | faulty control board | control_board | FALSE | TRUE | Other | Bad mcb | MGH96M060B3A | MGH96M | 5 |  | 2025-02-14 | 2025-12-11 | 300 | 31-365d | Please credit TPG Raynham | Contractor spoke with wholesaler about furnace. Tech at wholesaler diagnosed the with contractor. Board was replaced and now up and running. Please credit The Portland Group Raynham for a EAC17127600000708. |  |  |  | MGH96M060B3A |  | None;MCB | EAC17127600000708
22975 | 2025-12-20 | 2025 | 12 | 2025-12 | Motor | TRUE | medium | fan motor overload | mechanical | FALSE | TRUE | Protection | PA | EODA18H-48601 | EODA18H | 1.5 |  | 2019-12-31 | 2025-12-19 | 2180 | >2y | bad fan motor at the condenser | The caller, Jonathan from Gloria System, reported an error code PA on their heat system's condenser unit, indicating a potential issue with the fan motor overload protection. Mauricio Cordeiro requested the model and serial number of the unit, which Jonathan provided as EODA1801H460 and 101880, respectively. Mauricio instructed Jonathan to check the voltage going into the unit, which was confirmed to be 250 volts. Mauricio guided Jonathan through pressing buttons on the unit to check for error codes, confirming that the PA code indicated the gateway was not connected. Jonathan was advised to ensure the thermostat was set to heating mode, which he confirmed was set to 85 degrees Fahrenheit. After troubleshooting, Jonathan unplugged the unit and reconnected it, which temporarily resolved the issue, but the PA error returned. Mauricio suggested checking the wiring connections and confirmed that Jonathan did not have a ground wire connected. They discussed the wiring setup, and Jonathan confirmed he had the correct wires for the connection. Mauricio requested Jonathan's phone number to follow up with the office regarding the case. Tasks Jonathan is to ensure the thermostat is set to heating mode and check the wiring connections as instructed. Mauricio will follow up with the office regarding the case and Jonathan's phone number. |  | EODA18H-48601 | GN1836-P1 | na | 12670WIC560J21200076 | Fan Motor | EAC230904010
23014 | 2025-12-23 | 2025 | 12 | 2025-12 | MCB | TRUE | high | dead outdoor MCB | control_board | FALSE | TRUE | Other | No Display | EODA18H-2436 | EODA18H | 1.5 |  | 2023-08-12 | 2025-12-22 | 863 | >2y | Please credit Meier Supply Altoona PA | Issue 1: Outdoor Heat pump will not start . No Display Diagnosis Checked incoming voltage 246 volts in to EMI Filter, 246 out of EMI Filter Ohm Compressor, 1.0. 0.9, 0.9 Recommendation: Replace MCB |  | EODA18H-2436 |  |  | 1W123WM300ZM32300903 | None;MCB | EAC230904165
23023 | 2025-12-23 | 2025 | 12 | 2025-12 | Leakage | TRUE | high | evaporator coil leak | refrigerant | FALSE | TRUE | Other | na | EODA18H-2436 | EODA18H | 1.5 |  | 2023-05-22 | 2025-12-23 | 946 | >2y | coil leaking at air handler | The technician, Lawrence Jackson, reported that the heating and cooling unit was blowing cold air and confirmed that the refrigerant was low, indicating a leak in the evaporator coil. Mauricio Cordeiro requested the last six digits of the serial number of the Gateway to access necessary information, which was provided as 106313. Mauricio confirmed the address of the unit as 60 Winter Barrier Lane, Florence, Massachusetts, and acknowledged the need for a replacement evaporator coil. Mauricio provided the part number for the replacement coil as EAC10990500008 and instructed Jackson to contact their supply house to order the part. Mauricio stated that he would create a ticket number for warranty purposes and send a text message to Jackson with the part number and ticket number after the call. Tasks Mauricio will send a text message to Lawrence Jackson with the part number and ticket number within 5 to 10 minutes. Lawrence Jackson is to contact their supply house to order the replacement evaporator coil using the provided part number. |  | EODA18H-2436 | EAHATN-36 | na | 1A521WM400ZM41100332 |  | EAC1099000008
23027 | 2025-12-24 | 2025 | 12 | 2025-12 | Drain Pan | TRUE | medium | cracked drain pan | drain_water | FALSE | TRUE | Other | na | na | NA |  |  | 2025-01-27 | 2025-12-23 | 330 | 31-365d | cracked drain pan | The conversation involved a technical support call regarding a cracked drain pan for a unit. The outcome was the creation of a ticket and the commitment to send part and warranty information via text. Recap The technical support representative, Cameron Hebert, provided the model number EA ha tn-60 baa and the serial number 1 151 as NQ 400 Z Q4 150 0 0 8 6 for the unit in question. Mauricio Cordeiro confirmed the part number for the drain pan as e a c 230701514 and agreed to send a text message with the part and ticket number for warranty purposes. Cameron Hebert was instructed to take a picture of the cracked drain pan and send it to Mauricio after receiving the part number and ticket number. Tasks Mauricio Cordeiro will text Cameron Hebert the part number and warranty number within 10 minutes. Cameron Hebert will send a picture of the cracked drain pan to Mauricio after receiving the part number. |  | na | EAHATN-60BAA | na | na | Drain Pan 1 | EAc230701514
23028 | 2025-12-24 | 2025 | 12 | 2025-12 | Leakage | TRUE | high | refrigerant leak at coil | refrigerant | FALSE | TRUE | Other | No code | EODA18H-2436 | EODA18H | 1.5 |  | 2023-06-16 | 2025-12-22 | 920 | >2y | Ship coil to the address in the description box. | Ship coil to: Johnstone Supply 10620 METRIC BLVD AUSTIN TX , 78758 Tag for Strand Brothers. |  | EODA18H-2436 | na | na | 1G832WL400ZL40100308 | None;Evaporator assembly | EAC1099000008
23031 | 2025-12-24 | 2025 | 12 | 2025-12 | MCB | TRUE | high | failed outdoor PCB | control_board | FALSE | TRUE | Other | na | >ODA19H-2436AAA | >ODA19H- | 2 |  | 2025-11-01 | 2025-12-23 | 52 | 31-365d | bad board at outdoor unit | The conversation focused on troubleshooting a malfunctioning heat pump system, resulting in the identification of a potential issue with the outdoor board and the recommendation to order a replacement part. Recap The caller reported that one of their two heat pump systems was not functioning, while the other was operational, despite both being wired the same way. Mauricio Cordeiro guided the caller through troubleshooting steps, confirming that the outdoor unit was receiving 25 volts but the board was not responding, indicating a possible issue with the outdoor board. Mauricio instructed the caller to bypass the zone board and check for continuity in the wiring, which revealed no continuity between certain connections, further suggesting a problem with the board. Mauricio decided to create a ticket for the caller to order a new board and provided instructions on how to contact the supplier, including the part number and warranty process. Tasks The caller is to send Mauricio their name, company name, and pictures of the model number and surge protector for ticket creation. The caller is to contact the Portland Group to order the replacement board using the part number provided by Mauricio. |  | >ODA19H-2436AAA | na | na | OEWH003523Z24A160042 | MCB | EAC230904173
23083 | 2025-12-30 | 2025 | 12 | 2025-12 | E-code | TRUE | high | indoor outdoor communication error | communication | FALSE | FALSE | Control Board | E0 | EODA19H-2436AAA | EODA19H | 2 |  | 2024-10-21 | 2025-12-29 | 434 | 1-2y | E0 Error | E0 Error |  | EODA19H-2436AAA | EAHATN-36BAA | . | 0EWH003129Z243150058 | MCB | EAC230904173
23089 | 2025-12-30 | 2025 | 12 | 2025-12 | Gas Furnace | TRUE | medium | defective condensate trap | drain_water | FALSE | TRUE | Other | na | na | NA | [5 empty] | unknown | site visit for trap replacement | replaced bad trap with new hoses .tested system for 30 minutes .running normal |  | na | na | MGH96M080B3A | na |  | na
23093 | 2025-12-30 | 2025 | 12 | 2025-12 | MCB | TRUE | high | outdoor unit control board | control_board | FALSE | TRUE | Refrigerant Circuit | C8/E0 | EODA18H2436AAA | EODA18H | 1.5 |  |  |  |  | unknown | bad board on outdoor unit | Mauricio Cordeiro confirmed the EOD number as 198 and discussed the C8 and E0 alarms, noting that the C8 alarm was zero and there was no light on it. They identified the Gateway number as 301 and the error code as C8 bar, E Z, while also mentioning the part number needed as A C 230. The participant expressed gratitude for the information provided, indicating a successful exchange of technical details and specifications. Tasks Mauricio Cordeiro is to ensure the part number A C 230 is provided as needed. The participant is to follow up with any additional questions or clarifications regarding the discussed specifications. |  | EODA18H2436AAA | na | na | 0WEH0031282243130048 |  | EAC230904171
23101 | 2025-12-30 | 2025 | 12 | 2025-12 | MCB | TRUE | high | faulty control board | control_board | FALSE | TRUE | Refrigerant Circuit | C3/E0 | EODA19H4860AAA | EODA19H | 4 |  |  | 2025-12-29 |  | unknown | bad board at outdoor unit | Mauricio guided Jimmy through a series of diagnostic steps to check the compressor's performance, including measuring voltage and resistance across various wires. They determined that the compressor was experiencing high voltage issues, specifically noting a reading of 236 volts, which was acceptable. After checking the resistance values between the wires, they concluded that the control board was faulty and needed replacement. Mauricio provided Jimmy with a part number for the new control board and instructed him to contact FW Webb Supply to order it. Jimmy was asked to send pictures of the model number, serial number, and surge protector for warranty processing. Tasks Jimmy is to call FW Webb Supply to order the new control board using the part number provided by Mauricio. Jimmy needs to send Mauricio pictures of the model number, serial number, and surge protector to facilitate warranty processing. |  | EODA19H4860AAA | na | na | OEWH00424Z24506003 | MCB | EAC230904171
23110 | 2025-12-31 | 2025 | 12 | 2025-12 | Noise | TRUE | medium | contaminated refrigerant or moisture | refrigerant | TRUE | FALSE | Other | na | EODA18H 2436 BAA | EODA18H | 1.5 |  |  | 2025-12-30 |  | unknown | site visit for noise on condenser . | contractor reported noise on one EODA18H 2436BAA condenser .a week prior i gave him a EEV chip to install because that condenser is one of the list .after installing the chip the noise continued and system was not heating properly .today at my arrival contractor removed the freon and replaced filter dryer .added new freon . after starting the unit the noise went away .system was heating properly . |  | EODA18H 2436 BAA | na | na | 1400220IOCW1324H00004 |  | na
23120 | 2025-12-31 | 2025 | 12 | 2025-12 | MCB | TRUE | high | grounded compressor | mechanical | FALSE | TRUE | Refrigerant Circuit | C9 | EODA18H-2436 | EODA18H | 1.5 |  | 2020-06-23 | 2025-12-31 | 2017 | >2y | Grounded compressor ( 02/04/26), bad board on outside unit | The technician, Ryan, reported an issue with an HVAC unit (EODA 18H-2436) that was not running properly after replacing the section line temperature sensor, resulting in a C9 error code. Mauricio confirmed that the compressor was not receiving DC voltage and suggested that the issue might be due to the compressor terminals being unplugged, which was confirmed by Ryan. After checking the system's power supply, Ryan reported 240 volts, which was acceptable, but the unit still failed to operate correctly, indicating a need for further investigation. Mauricio diagnosed the problem as likely being a faulty control board and provided Ryan with the part number and instructions to contact the supply house, F.W. Webb, for the replacement part. Mauricio committed to texting Ryan the part number and claim number for the control board after the call, ensuring Ryan had the necessary information to proceed with the repair. Tasks Mauricio will text Ryan the part number and claim number for the control board replacement after the call. Ryan is to contact F.W. Webb to check for the availability of the control board. |  | EODA18H-2436 | EAHATN-36 | na | 11649WJ4290J60100063 |  | 231235530 (02/04/26), EAC230904173
23125 | 2026-01-01 | 2026 | 1 | 2026-01 | Leakage | TRUE | high | indoor coil leak | refrigerant | FALSE | TRUE | Other | na | EODA18H -2436 | EODA18H | 1.5 |  |  | 2025-12-31 |  | unknown | Leaky Coil | Leaky Coil |  | EODA18H -2436 | EAHATN-36 |  | 10372WL800ZL80300014 | Evaporator Only | EAC1099000008
23144 | 2026-01-03 | 2026 | 1 | 2026-01 | MCB | TRUE | high | defective outdoor PCB | control_board | FALSE | TRUE | Communication | h2 | EODA18H-2436 | EODA18H | 1.5 |  | 2021-01-19 |  |  | unknown | bad board on the outdoor unit | The conversation involved troubleshooting an error code H2 related to a sensor, which was resolved by removing the ambient temperature control and obtaining readings for the sensor. The outcome confirmed the sensor was functioning correctly after adjustments were made. Recap The main issue discussed was the error code H2, which was resolved by removing the ambient temperature control, allowing the system to operate in back-off mode. The sensor was tested, and a reading of 45.4 was obtained, which was within the acceptable range of 0.5 to 350k ohms, confirming its functionality. The second sensor, referred to as sock stream 1, was also discussed, but no specific readings were provided for it during the call. Tasks MEJIA LEANDRO is to monitor the readings for the sock stream 1 sensor and report back if necessary. |  | EODA18H-2436 | EAHATN-36 | na | 16015WK415ZK60300094 | MCB | Eac 230904173
23191 | 2026-01-06 | 2026 | 1 | 2026-01 | MCB | TRUE | high | failed outdoor MCB | control_board | FALSE | TRUE | Other | na | EODA18H-4860 | EODA18H | 1.5 |  | 2023-06-15 | 2026-01-06 | 936 | >2y | blank board on condenser with surge protector installed | The technician reported no power to the board despite having incoming power, and the Gateway was offline. Mauricio confirmed the issue and began troubleshooting steps. Mauricio instructed the technician to measure the voltage at the board and confirmed readings of 24 and 34 volts at various points, indicating a potential issue with the board. The technician provided the last six digits of the Gateway's serial number, which was 3000111, allowing Mauricio to access additional information. Alerts were identified on the unit, including module protection issues, and Mauricio asked if a surge protector was in place, which the technician confirmed. Mauricio directed the technician to disconnect three compressor wires (blue, red, and blue/white) for further testing and instructed them to take a picture of the meter reading, which was confirmed to be normal at 0.5. The technician was instructed to check if the compressor was grounded by testing each wire against the ground, which confirmed it was not grounded. Mauricio requested the technician to reconnect the wires and power the compressor back on, then take a picture of the meter reading of 244 volts at L1 and L2 for warranty purposes. Mauricio planned to send a text message with a part number for the board to the technician, who would then call the Portland group to order it. A ticket number for the warranty process was to be created by Mauricio, which the technician would use when returning the old board for reimbursement. Tasks Mauricio will send a text message with the part number for the board to the technician. Mauricio will create a ticket number for the warranty process and send it to the technician. The technician is to take a picture of the meter reading of 244 volts at L1 and L2 after powering the compressor back on. The technician is to take a picture of the surge protector and send it back to Mauricio. |  | EODA18H-4860 | EAHATN-60 | na | 1A681WM600ZM60500316 | MCB | EAC230904171
23194 | 2026-01-06 | 2026 | 1 | 2026-01 | MCB | TRUE | high | EEPROM chip failure | control_board | FALSE | TRUE | Control Board | E0 | EODA18H-2436BAA | EODA18H | 1.5 |  | 2024-10-31 | 2026-01-06 | 432 | 1-2y | bad board with E0 error code and surge protector installed | The technician, Sierra Hughes, provided the last six digits of the unit's serial number as 70147, which was used to look up error codes. It was determined that the system had been locked out since December 26th, and the unit was experiencing heating issues. Mauricio Cordeiro identified an error code (E0) indicating a problem with the board and suggested that a chip might be needed. Sierra confirmed the presence of a surge protector and provided the age of the house as new, which led to a discussion about surge protectors being required by law in Massachusetts. Mauricio instructed Sierra to check the voltage readings at various points in the unit, which were found to be within acceptable ranges (L1 and L2 readings of 237 and 238). Sierra was directed to power off the unit and disconnect the compressor wires for further testing. Continuity tests were performed on the compressor wiring, revealing no continuity, indicating a bad board. Mauricio requested Sierra to take pictures of the voltage readings and the connections for documentation purposes due to company policy. The conversation included a discussion about the high cost of replacement boards, with the smaller board priced at approximately $1500 and the larger at $1900. Mauricio agreed to send Sierra the part number and create a warranty ticket after receiving the necessary pictures. Tasks Sierra Hughes is to send pictures of the surge protector and voltage readings to Mauricio Cordeiro. Mauricio Cordeiro will text Sierra the part number and create a warranty ticket for the board replacement. Sierra is to contact the Portland Group to order the replacement board using the provided part number. |  | EODA18H-2436BAA | EAHATN-24 | na | 1402220IOCW13246L000112 | MCB | EAC230904173
23197 | 2026-01-06 | 2026 | 1 | 2026-01 | Leakage | TRUE | high | evaporator coil leak | refrigerant | FALSE | TRUE | Other | na | EODA18H-4860 | EODA18H | 1.5 |  | 2023-12-17 | 2026-01-06 | 751 | >2y | Coil leak on indoor unit | Fernando from Homeworks Energy reported a leaky coil and inquired about the warranty for it. Mauricio confirmed the company name and began troubleshooting the issue. Mauricio requested the last six digits of the coil's serial number, which Fernando provided as 300490, and confirmed the address as 127 Circle in Stoneham, Mass. Fernando explained that the leak was detected using an electric detector, and Mauricio requested a 5-second video of the leak for record-keeping. Mauricio indicated that he would send Fernando a text with the part number and create a ticket number for the warranty, ensuring that Fernando could get reimbursement for the coil when returning the old one. Tasks Fernando will send Mauricio a video of the leak for record-keeping. Mauricio will send Fernando a text with the part number and a ticket number for the warranty within 5 to 10 minutes. |  | EODA18H-4860 | EAHATN-60 | na | 1W967WM700ZM71700459 | Evaporator assembly | EAC1099000009
23210 | 2026-01-07 | 2026 | 1 | 2026-01 | Leakage | TRUE | high | evaporator coil leak | refrigerant | FALSE | TRUE | Other | na | na | NA |  |  |  | 2026-01-06 |  | unknown | coil leak at indoor unit | Tech Support - Pereira Jacob requested a case number for an Eco unit with a leaking coil, which they verified using soap and a leak detector. Mauricio Cordeiro instructed Tech Support - Pereira Jacob to send a picture of the bubbles from the leak and the model number of the air handler to proceed with the case. Mauricio Cordeiro confirmed their phone number as 5714 918318 for further communication regarding the case. Tasks Tech Support - Pereira Jacob is to send a picture of the bubbles from the leak and the model number of the air handler to Mauricio Cordeiro. |  | na | EAHTN 36 BAA | na | na | Evaporator assembly | EAC1099000008
23213 | 2026-01-07 | 2026 | 1 | 2026-01 | Leakage | TRUE | high | leaking evaporator coil | refrigerant | FALSE | TRUE | Other | na | EODA18H-4860 | EODA18H | 1.5 |  | 2023-11-12 | 2026-01-06 | 786 | >2y | coil leak at indoor coil | Mike from Glasco Heating and Cooling called to inquire about warranty service for a unit showing an alert code for severely undercharged refrigerant and a leaking evaporator coil. Mauricio confirmed the presence of a Gateway on the unit and requested the last six digits of its serial number to assist in locating the necessary part information. The address for the service was confirmed as 18 Oakmore Drive, Vernon, Connecticut, for customer Colleen Mackey. Mauricio identified the part number for the coil and noted that Mike's company typically sources parts from FW Webb or Wind Supply in Connecticut. Mauricio committed to sending Mike a text message with the part number and creating a ticket number for the warranty call after their conversation. Mike agreed to send a 5-second video of the leak check results to Mauricio for further assessment, and Mauricio assured him that he would text from his cell phone for any follow-up communication. Tasks Mauricio will send Mike a text message with the part number for the warranty claim. Mauricio will create a ticket number for Mike's warranty call. Mike will send a 5-second video of the leak check results to Mauricio. |  | EODA18H-4860 | GNC3036BPT | MGH96M060B3A | 1W967WM600ZM60100860 | Evaporator assembly | EAC1099000008
23215 | 2026-01-07 | 2026 | 1 | 2026-01 | MCB | TRUE | high | failed inverter board | control_board | FALSE | TRUE | Control Board | E0/ P7/CC/C9 | EODA 18H 2436 | EODA | 1.5 |  |  | 2026-01-06 |  | unknown | bad board at condenser .asked contractor to install surge protector with new board. also bad high pressure sensor | The technician, Jason from Colonie Mechanical Contractors, reported issues with an EODA 18H-2436 unit at the Hampton Inn, including error codes E7 and E0, indicating potential mechanical failure of the compressor. Mauricio Cordeiro guided Jason through diagnostic steps, confirming that the compressor was not starting and that the high-pressure sensor (F7) was likely malfunctioning. Mauricio advised Jason to take pictures of the model and serial numbers for warranty purposes and to check the voltage and ohm readings on the compressor wires. Jason was instructed to order a new inverter board and a high-pressure sensor from their usual supply house, with Mauricio providing part numbers and warranty information. Mauricio emphasized the importance of installing a surge protector when replacing the board to prevent future damage and advised Jason to document the process with pictures for warranty claims. Tasks Jason is to take pictures of the model and serial numbers of the HVAC unit and send them to Mauricio for warranty verification. Jason is to order a new inverter board and high-pressure sensor from their supply house, using the part numbers provided by Mauricio. Jason is to ensure a surge protector is installed when replacing the board to prevent future issues |  | EODA 18H 2436 | na | na | 1W123WM100ZM11600217 |  | EAC230904173/EAC231235159
23222 | 2026-01-07 | 2026 | 1 | 2026-01 | BAD ODU | TRUE | medium | improper backup switchover | electrical | FALSE | TRUE | Compressor | low voltage issue | EODA18H-2436 | EODA18H | 1.5 |  | 2021-05-19 |  |  | unknown | System is not switching over to back up. | The system is not switching over to back up. Even when the furnace is on, the condenser fan motor is running outside. |  | EODA18H-2436 | Rheem Furnace |  | 12673WK252ZK51900067 | MCB;Thermostat | EAC230904173, EST02
23226 | 2026-01-08 | 2026 | 1 | 2026-01 | EEV | TRUE | medium | bad EEV coil | mechanical | FALSE | TRUE | Other | na | EODA18H 2436 | EODA18H | 1.5 |  |  | 2026-01-07 |  | unknown | bad eev coil on condenser | Tech Support reported a customer with two Eco units, one of which is making a loud thumping noise, similar to a compressor issue. They previously replaced the control board on the other unit to resolve a similar problem. Mauricio requested the model and serial numbers of the malfunctioning unit, which Tech Support agreed to send. The age of the problematic system was confirmed to be two years old, and both parties discussed the symptoms and potential causes of the noise. Mauricio guided Tech Support through checking the compressor speed and pressure readings, which indicated normal operation but raised concerns about the noise. Tech Support provided their address as 1 Sunset Lane, and Mauricio offered to meet them there to further investigate the issue, agreeing to arrive shortly despite the rain. Tasks Tech Support will send Mauricio the model and serial numbers of the Eco unit. Mauricio will meet Tech Support at 1 Sunset Lane to investigate the noise issue further. |  | EODA18H 2436 | na | na | 1W123WM300ZM32301101 | Other | EAC3120290034
23227 | 2026-01-08 | 2026 | 1 | 2026-01 | MCB | TRUE | high | main control board failure | control_board | FALSE | TRUE | Other | na | EODA 18H 4860 | EODA | 1.5 |  |  | 2026-01-07 |  | unknown | blank board at condenser | The conversation involved troubleshooting an outdoor unit issue with Phillip, a contractor, who reported that the unit was not initializing. The outcome was a diagnosis indicating a likely bad board, with instructions for further testing and follow-up actions. Recap Phillip reported that the outdoor unit was not initializing, while the indoor unit was functioning correctly. Mauricio guided Phillip through troubleshooting steps to diagnose the issue. Phillip provided the model number of the outdoor unit as EODA 18H-4860, which is about a year old. Mauricio confirmed that these are brand new units and inquired about the presence of a surge protector. Mauricio instructed Phillip to perform voltage tests on the unit, confirming readings of 215 volts on both high and low voltage lines, indicating that the voltage levels were acceptable. After further testing, Phillip found no continuity from the compressor wires to ground, leading Mauricio to conclude that the board was likely faulty. Mauricio advised Phillip to take pictures of the multimeter readings and the unit's model and serial numbers for warranty purposes, emphasizing the need for proper documentation. Mauricio instructed Phillip to contact the Portland group to check on the availability of a replacement board and to inquire about the timeline for delivery, suggesting that if it was not available by Saturday, Phillip could pick one up from Mauricio's location. Mauricio explained the process for returning the old board and obtaining credit for the new one, emphasizing the importance of following the warranty procedures and keeping communication open for any future issues. Tasks Phillip is to take pictures of the multimeter readings and the model and serial numbers of the unit and send them to Mauricio for warranty documentation. Phillip is to contact the Portland group to check on the availability of a replacement board and its delivery timeline. If the board is not available by Saturday, Phillip is to arrange to pick up a board from Mauricio's location. |  | EODA 18H 4860 | na | na | 1w967WM600ZM61200169 | MCB | Eac230904171
23234 | 2026-01-08 | 2026 | 1 | 2026-01 | Leakage | TRUE | high | evaporator coil leak | refrigerant | FALSE | TRUE | Other | none | . | . |  |  | 2020-11-18 |  |  | unknown | Coil Leak | Coil Leak |  | . | EAHATN-36 |  | . | Evaporator Only | EAC1099000008
23235 | 2026-01-08 | 2026 | 1 | 2026-01 | Leakage | TRUE | high | evaporator coil leak | refrigerant | FALSE | TRUE | Other | none | . | . |  |  | 2020-11-18 |  |  | unknown | Coil Leak 2nd unit | Coil Leak |  | . | EAHATN-36 |  | . | Evaporator Only | EAC1099000008
23238 | 2026-01-08 | 2026 | 1 | 2026-01 | Top Cover | TRUE | high | fan motor assembly failure | mechanical | FALSE | TRUE | Other | na | EODA18H4860 | EODA18H | 1.5 |  |  |  |  | unknown | damaged top part of condenser due to fan assembly came apart | The technician, Fisher Karl, reported that the top metal housing of the fan unit cracked, damaging some bolts and possibly the coil, with model number E0DA18HD4860 and serial number 1G261W1ZL1280010 provided for reference. Mauricio Cordeiro requested pictures of the damage and confirmed that they would create a ticket number for the parts needed, including a fan motor, blade, and top housing. Fisher Karl confirmed that they have a picture of the damage and will send it via text message, while also providing their location in Easton, Massachusetts, and the company name, Fischer Heating and Air Conditioning Incorporated. Mauricio Cordeiro mentioned having a spare condenser at their house that could be used if parts are delayed, and they agreed to send part numbers to Fisher Karl for ordering through FW Webb. Tasks Fisher Karl will send pictures of the damaged unit via text message. Mauricio Cordeiro will create a ticket number and find the necessary part numbers to send to Fisher Karl. If parts are delayed, Mauricio Cordeiro will offer the spare condenser for use. |  | EODA18H4860 | na | na | 1G261WL100ZL12800110 | Other | 230803000
23265 | 2026-01-09 | 2026 | 1 | 2026-01 | Leakage | TRUE | high | evaporator coil leak | refrigerant | FALSE | TRUE | Other | NONE | EAHATN-24 | EAHATN | 2 |  |  |  |  | unknown | LEAKY COIL | Coil Leak |  |  | EAHATN-24 |  |  | Evaporator assembly | EAC1099000008
23288 | 2026-01-10 | 2026 | 1 | 2026-01 | Top Cover | TRUE | high | fan motor assembly failure | mechanical | FALSE | TRUE | Other | na | EODA18H2436 | EODA18H | 1.5 |  |  |  |  | unknown | damaged top part of condenser due to fan assembly came apart number 4 | The technician, Fisher Karl, reported that the top metal housing of the fan unit cracked, damaging some bolts and possibly the coil, with model number E0DA18HD4860 and serial number 1G261W1ZL1280010 provided for reference. Mauricio Cordeiro requested pictures of the damage and confirmed that they would create a ticket number for the parts needed, including a fan motor, blade, and top housing. Fisher Karl confirmed that they have a picture of the damage and will send it via text message, while also providing their location in Easton, Massachusetts, and the company name, Fischer Heating and Air Conditioning Incorporated. Mauricio Cordeiro mentioned having a spare condenser at their house that could be used if parts are delayed, and they agreed to send part numbers to Fisher Karl for ordering through FW Webb. Tasks Fisher Karl will send pictures of the damaged unit via text message. Mauricio Cordeiro will create a ticket number and find the necessary part numbers to send to Fisher Karl. If parts are delayed, Mauricio Cordeiro will offer the spare condenser for use. |  | EODA18H2436 | na | na | 1WM300ZM2301068 | Other | 230803000
23289 | 2026-01-10 | 2026 | 1 | 2026-01 | Top Cover | TRUE | high | fan assembly failure | mechanical | FALSE | TRUE | Other | na | EODA18H2436 | EODA18H | 1.5 |  |  |  |  | unknown | damaged top part of condenser due to fan assembly came apart number 3 | The technician, Fisher Karl, reported that the top metal housing of the fan unit cracked, damaging some bolts and possibly the coil, with model number E0DA18HD4860 and serial number 1G261W1ZL1280010 provided for reference. Mauricio Cordeiro requested pictures of the damage and confirmed that they would create a ticket number for the parts needed, including a fan motor, blade, and top housing. Fisher Karl confirmed that they have a picture of the damage and will send it via text message, while also providing their location in Easton, Massachusetts, and the company name, Fischer Heating and Air Conditioning Incorporated. Mauricio Cordeiro mentioned having a spare condenser at their house that could be used if parts are delayed, and they agreed to send part numbers to Fisher Karl for ordering through FW Webb. Tasks Fisher Karl will send pictures of the damaged unit via text message. Mauricio Cordeiro will create a ticket number and find the necessary part numbers to send to Fisher Karl. If parts are delayed, Mauricio Cordeiro will offer the spare condenser for use. |  | EODA18H2436 | na | na | 1WM300ZM32301036 | Other | 230803000
23290 | 2026-01-10 | 2026 | 1 | 2026-01 | Top Cover | TRUE | high | fan assembly failure | mechanical | FALSE | TRUE | Other | na | EODA18H4860 | EODA18H | 1.5 |  |  |  |  | unknown | damaged top part of condenser due to fan assembly came apart number 2 | The technician, Fisher Karl, reported that the top metal housing of the fan unit cracked, damaging some bolts and possibly the coil, with model number E0DA18HD4860 and serial number 1G261W1ZL1280010 provided for reference. Mauricio Cordeiro requested pictures of the damage and confirmed that they would create a ticket number for the parts needed, including a fan motor, blade, and top housing. Fisher Karl confirmed that they have a picture of the damage and will send it via text message, while also providing their location in Easton, Massachusetts, and the company name, Fischer Heating and Air Conditioning Incorporated. Mauricio Cordeiro mentioned having a spare condenser at their house that could be used if parts are delayed, and they agreed to send part numbers to Fisher Karl for ordering through FW Webb. Tasks Fisher Karl will send pictures of the damaged unit via text message. Mauricio Cordeiro will create a ticket number and find the necessary part numbers to send to Fisher Karl. If parts are delayed, Mauricio Cordeiro will offer the spare condenser for use. |  | EODA18H4860 | na | na | 1J340WL400ZL40100239 | Other | 230803000
23291 | 2026-01-10 | 2026 | 1 | 2026-01 | IoT | TRUE | medium | faulty IoT gateway | communication | FALSE | TRUE | Other | na | EODA19H-4860AAA | EODA19H | 4 |  | 2026-01-02 | 2026-01-08 | 6 | ≤30d (infant) | bad gateway not connecting to system | The caller, Rob Schultz from FW Webb, reported that a communication kit (EG 910 L) failed to connect, requiring a replacement. They requested information on the warranty process. Mauricio Cordeiro confirmed that a ticket number (23291) was created for the warranty claim and advised that the contractor should call for support in the future when issues arise. The serial number of the faulty unit (GF 9102 3477 0.0.0 72) and the replacement unit (GF 91 0252 2 1 6 0) were recorded for reference. The address for the installation was confirmed as 27 Crosswinds, with the homeowner's name being David Miles. The contractor's name was confirmed as Benui Oil, with spelling assistance provided to ensure accuracy. Mauricio advised Rob to email support@eco.com for the warranty return goods authorization (RGA) and suggested transferring him to Selene for further assistance with the warranty process. Tasks Rob Schultz is to email support@eco.com to obtain the RGA for the warranty return. Rob is advised to ensure that the contractor calls for support in the future when issues arise. |  | EODA19H-4860AAA | EAHETN-60HA | na | 0EWH004522Z24A120008 | Other | gateway
23294 | 2026-01-10 | 2026 | 1 | 2026-01 | MCB | TRUE | high | outdoor PCB failure | control_board | FALSE | TRUE | Control Board | E0 | EODA18H-4860 | EODA18H | 1.5 |  | 2021-04-14 | 2026-01-09 | 1731 | >2y | bad board on outdoor unit .contractor will install surge protector | The caller reported an error code "E0" indicating an electronic problem with the outdoor unit, which was confirmed by Mauricio Cordeiro. Mauricio instructed the caller to switch the unit to heat mode and confirmed that the issue had been ongoing since Monday. The caller provided the last six digits of the serial number of the IoT device, which was noted for further investigation. Mauricio identified that the compressor was likely functioning correctly based on the voltage readings provided by the caller. The caller was asked to send a picture of the main board's model number for verification, which revealed that the board was an older version. Mauricio confirmed that a new board with improved features would be sent to the caller, and instructions for installation were discussed. The need for a surge protector was emphasized, and the caller agreed to inform their boss about this requirement. Mauricio requested the caller to take and send pictures of the voltage readings from the compressor for documentation purposes. Tasks The caller will send pictures of the voltage readings from the compressor to Mauricio. Mauricio will discuss the situation with their boss and arrange to send a new board to the caller. The caller will inform their boss about the need for a surge protector. |  | EODA18H-4860 | EAHATN-36 | na | 16015WK417ZK60300215 | MCB | EAC230904171
23297 | 2026-01-10 | 2026 | 1 | 2026-01 | Motor | TRUE | high | indoor blower motor failure | mechanical | FALSE | TRUE | Other | na | EODA18H-4860 | EODA18H | 1.5 |  | 2021-09-08 | 2026-01-09 | 1584 | >2y | bad blower motor on air handler | Mauricio Cordeiro contacted Tech Support to gather information about a problem with a unit reported by their boss, Joshua, who was traveling. Tech Support identified that the unit was experiencing an E1 code due to a malfunctioning fan motor that was not operating at the correct speed. Mauricio confirmed the need to replace the fan motor and requested the model and serial number of the indoor unit, which Tech Support provided as 1186. Mauricio offered to send a part number for the replacement fan motor, which they identified as EAC 230, and confirmed that the part would be shipped directly to Tech Support. Tech Support agreed to provide their company information, including name, email, and address, to facilitate the order and warranty ticket creation. Mauricio committed to creating a ticket for the warranty and sending the ticket number back to Tech Support for their records. |  | EODA18H-4860 | EAHATN-48 | na | 16015WK417ZK60300068 | Blower Motor | EAC 230904170
23298 | 2026-01-10 | 2026 | 1 | 2026-01 | MCB | TRUE | high | EEPROM parameter error | communication | FALSE | TRUE | Control Board | E0 | EODA19H-4860AAA | EODA19H | 4 |  | 2025-04-10 |  |  | unknown | E0 Error | E0 Error |  | EODA19H-4860AAA | EAHATN-60 | . | 0EWH004126Z244030002 | MCB | EAC230904171
23299 | 2026-01-10 | 2026 | 1 | 2026-01 | Motor | TRUE | medium | failed blower motor speed | mechanical | FALSE | TRUE | Other | na | . | . | [5 empty] | unknown | Blower Motor having issue. Suddenly stopped working. | Blower Motor having issue. Suddenly stopped working. Tech changed to high speed, motor did not stop running. |  | . | EAHATN-36 | . | . | Blower Motor | 230904148
23336 | 2026-01-13 | 2026 | 1 | 2026-01 | MCB | TRUE | high | dead outdoor control board | control_board | FALSE | TRUE | Other | BLANK DISPLAY | EODA18H-4860 | EODA18H | 1.5 |  | 2022-04-27 |  |  | unknown | blank display on screen | blank display on screen, compressor ohm good. 0.4, 0.4, 0.3 |  | EODA18H-4860 | . | . | 1O608WL900ZL92600189 | MCB | EAC230904171
23344 | 2026-01-13 | 2026 | 1 | 2026-01 | MCB | TRUE | high | faulty main control board | control_board | FALSE | TRUE | Control Board | E0 | EODA18H-4860 | EODA18H | 1.5 |  |  | 2026-01-13 |  | unknown | FAULTY CONTROL BOARD | FAULTY CONTROL BOARD, TECH OVER WITH JOSHUA ON THE PHONE ON 6/12/25. |  | EODA18H-4860 | . | . | 1A681WM600ZM60500438 | MCB | EAC230904166
23351 | 2026-01-14 | 2026 | 1 | 2026-01 | MCB | TRUE | high | failed outdoor pcb | control_board | FALSE | TRUE | Other | na | EODA18H4860 | EODA18H | 1.5 |  | 2022-04-29 | 2026-01-13 | 1355 | >2y | blank board on outdoor unit with surge protector installed | The caller, identified as Jay from Boston Standard, reported a malfunctioning control board for an HVAC system, confirming a voltage reading of 239.9 volts at the board, which indicated a potential issue with the control board as there was no LED light displayed. Mauricio Cordeiro instructed Jay to take a picture of the voltage reading and mentioned that this was the second time a bad board had been reported, noting that a surge protector had been installed after the first replacement. Jay confirmed that a different technician had been sent previously to find a leak but was unsuccessful, and Mauricio requested pictures of the model number and surge protector for further assistance. Mauricio provided Jay with a part number (EA230) to order a new board from their usual supplier, FWF, and advised Jay to check the installation date of the unit, which was confirmed to be April 29, 2022. Mauricio informed Jay that he would create a ticket for warranty purposes and reminded him to read the instructions that come with the new board regarding necessary adaptations for installation. Tasks Jay is to take a picture of the voltage reading and send it to Mauricio. Jay is to send pictures of the model number and surge protector to Mauricio. Jay is to order the new board using the provided part number (EA230) from FWF. Mauricio will create a warranty ticket for Jay and send him the ticket number. |  | EODA18H4860 | na | na | 1068WL900ZL92600133 | MCB | EAC230904171
23380 | 2026-01-15 | 2026 | 1 | 2026-01 | BAD ODU | TRUE | medium | refrigerant overcharge and static pressure | refrigerant | TRUE | FALSE | unknown |  | EODA19H2436AAA | EODA19H | 2 |  | 2025-12-23 | 2026-01-14 | 22 | ≤30d (infant) | frozen condenser coil | found condenser coil frozen .adjusted static pressure on the indoor unit to .5 it was too high .removed 5 OZ freon from system .tested system running normal . |  | EODA19H2436AAA | EAHAEC-36 | na | OEW003523Z24A160042
23381 | 2026-01-15 | 2026 | 1 | 2026-01 | BAD ODU | TRUE | high | undersized control transformer | electrical | TRUE | FALSE | unknown |  | EODA19H2436AAA | EODA19H | 2 |  | 2026-01-06 | 2026-01-13 | 7 | ≤30d (infant) | brand new install .condenser wont turn on | at arriving found 25 volts at Y and C wire at condenser but after connecting the wires into the condenser found that the voltage dropped to 16 .found out that transformer at Concord furnace was powering the furnace board and the zone panel with 3 zones connected also powering the dual fuel relay and the board outside .had electrician ad a separate transformer to help with the load .tested system running properly . |  | EODA19H2436AAA | na | na | OEWH003523Z24A160042
23388 | 2026-01-16 | 2026 | 1 | 2026-01 | Blower | TRUE | high | faulty blower motor | mechanical | FALSE | TRUE | Control Board | E0 | . | . |  |  |  | 2026-01-15 |  | unknown | Faulty Blower | Faulty Blower |  | . | EAHETN-60HA | . | . | Blower Motor | 883259F
23411 | 2026-01-17 | 2026 | 1 | 2026-01 | Leakage | TRUE | high | evaporator coil leak | refrigerant | FALSE | TRUE | Other | na | . | . |  |  |  | 2026-01-16 |  | unknown | COIL LEAK | COIL LEAK, PERFORMED ISOLATION TEST AND FOUND LEAK IN THE EVAP COIL |  | . | EAHATN-24 | . | . | Evaporator Only | EAC1099000008
23460 | 2026-01-20 | 2026 | 1 | 2026-01 | Bad AHU | TRUE | medium | indoor unit board failure | control_board | FALSE | TRUE | Control Board | Emergency heat not working | EAHATN-60 | EAHATN | 5 |  | 2025-05-08 | 2026-01-19 | 256 | 31-365d | Please credit TPG Soco ME | Need new IDU board will be sipping a replacement. |  |  | EAHATN-60 |  |  | MCB | eac230901221
23462 | 2026-01-20 | 2026 | 1 | 2026-01 | MCB | TRUE | high | failed indoor control board | control_board | FALSE | TRUE | Other | No lights on control board. System not working. | EAHDEN-36ABA | EAHDEN | 3 |  | 2025-12-19 | 2026-01-18 | 30 | ≤30d (infant) | Please credit FW Webb Hyannis | Contractor called to home for no heat. System was not working. Indoor unit does not react to call. Lights on control board are no longer blinking. He is swapping out the IDU board. FW Webb ordered him one on PO 3-05049049 |  |  | EAHDEN-36ABA |  |  | None;MCB | EAC230906001
23474 | 2026-01-20 | 2026 | 1 | 2026-01 | Compressor | TRUE | high | internal compressor failure | mechanical | FALSE | TRUE | Refrigerant Circuit | C4 | EODA18H-4860 | EODA18H | 1.5 |  | 2022-04-20 | 2026-01-20 | 1371 | >2y | faulty compressor C4 error | faulty compressor running like theres rocks in the system. |  | EODA18H-4860 | . | . | 1O608WL800ZL81600609 | Compressor;MCB | 231235532 & EAC230904171
23490 | 2026-01-21 | 2026 | 1 | 2026-01 | MCB | TRUE | high | main control board failure | control_board | FALSE | TRUE | Protection | P9 | EODA18H-2436BAA | EODA18H | 1.5 |  | 2024-05-17 |  |  | unknown | P9 Error | P9 Error. Troubleshot with Ess Pro app. Telling it needs a MCB. |  | EODA18H-2436BAA | . | . | 14ZU0WP500ZP52500315 | MCB | EAC230904173
23508 | 2026-01-21 | 2026 | 1 | 2026-01 | E-code | TRUE | high | shorted compressor windings | electrical | FALSE | TRUE | Control Board | E0 | EODA19H -4860AAA | EODA19H | 4 |  | 2025-12-01 | 2026-01-21 | 51 | 31-365d | E0 error | E0 error homs reading: .4, .5, .5 | E0 | EODA19H -4860AAA | . | . | 0EWH004125Z243180039 | MCB | EAC230904171
23535 | 2026-01-23 | 2026 | 1 | 2026-01 | MCB | TRUE | high | burnt EMI filter | control_board | FALSE | TRUE | Other | na | EODA18H-4860 | EODA18H | 1.5 |  | 2022-01-28 |  |  | unknown | Burnt EMI filter | Burnt EMI filter |  | EODA18H-4860 | . | . | 1W967WM400ZM40100334 | EMi Filter | 230904159
23537 | 2026-01-23 | 2026 | 1 | 2026-01 | E-code | TRUE | high | compressor short to ground | electrical | FALSE | TRUE | Control Board | E0 | EODA18H-4860BAA | EODA18H | 1.5 |  | 2025-01-11 | 2026-01-22 | 376 | 1-2y | E0 Error | E0 error. Compressor ohms 2, 2, 2. Opento ground on all wires. | E0 | EODA18H-4860BAA | . | . | 166I4WQ500ZQ51200005 | MCB | EAC230904171
23546 | 2026-01-23 | 2026 | 1 | 2026-01 | Motor | TRUE | high | faulty blower motor | mechanical | FALSE | TRUE | Compressor | Leak in Coil | . | . |  |  |  | 2026-01-22 |  | unknown | Faulty blower motor | Faulty blower motor, per joshua, approved this replacemnet. |  | . | . | MGH96M100C5A | . | Blower Motor | 11002015011987
23624 | 2026-01-27 | 2026 | 1 | 2026-01 | Gas Furnace | TRUE | medium | incorrect thermostat wiring | electrical | TRUE | FALSE | Other | na | na | NA | [5 empty] | unknown | bad gas valve at furnace | The caller, identified as Thomas, reported a gas valve issue in their furnace, stating they had 3.4 volts at the gas valve but it would not open. Mauricio confirmed that 24 volts is required to open the gas valve and discussed troubleshooting steps. Mauricio explained that the NL code was due to a wiring issue related to the dual fuel kit, which is necessary for the furnace setup. They discussed the need for a dual fuel kit to separate the connections properly. Thomas mentioned that he had disconnected the condenser and was attempting to troubleshoot the furnace directly from the thermostat. Mauricio guided him through the process of jumping wires to test the system. They identified that the gas valve should receive 24 volts and discussed the wiring connections, with Mauricio suggesting that a faulty pressure switch might be causing the issue. Mauricio provided Thomas with a part number for the gas valve (EAC 12174 276 0 0 0 0 1 1389) and advised him to contact a local distributor for a rush order on the part. Tasks Thomas is to send a picture of the furnace model number and serial number to Mauricio for warranty processing. Mauricio will create a ticket number for Thomas's warranty claim once he receives the necessary information. |  | na | na | MGH96M100C5A | na | Gas valve | EAC17427600001389 & 17127600000708
23640 | 2026-01-27 | 2026 | 1 | 2026-01 | Compressor | TRUE | high | failed compressor windings | mechanical | FALSE | TRUE | Refrigerant Circuit | C2/C7/C3 | EODA18H4860 | EODA18H | 1.5 |  |  | 2026-01-27 |  | unknown | bad compressor .Ohms reading (0.4/0.7/1.7) | Daniel (Customer) reported issues with the system's performance over the last few days. Mauricio (Technical Support Representative) confirmed the system's gateway was replaced last month. Error codes C2, C3, and C7 were identified, suggesting potential compressor issues. Daniel provided voltage readings from the system, which were checked by Mauricio. Mauricio instructed Daniel on how to test the compressor wires for continuity. Inconsistent readings from the compressor indicated a possible malfunction. Mauricio suggested the unit might be under warranty based on its installation date. Daniel was advised to take pictures for warranty documentation and further troubleshooting. Mauricio committed to providing a ticket number for warranty claims and necessary part information. The conversation ended with Daniel thanking Mauricio for the assistance. |  | EODA18H4860 | na | na | 1A681WM600ZM60500509 | Compressor | EAC231235532
23642 | 2026-01-27 | 2026 | 1 | 2026-01 | Leakage | TRUE | high | evaporator coil leak | refrigerant | FALSE | TRUE | Other | na | EODA18H-2436BAA | EODA18H | 1.5 |  | 2024-03-06 | 2026-01-27 | 692 | 1-2y | Coil Leak/also leak at the suction side valve | Coil Leak |  | EODA18H-2436BAA | GNC2430BPT | . | 14ZU0WP500ZP52500263 | Evaporator assembly | GNC2430BPT/EAC231231468
23647 | 2026-01-28 | 2026 | 1 | 2026-01 | MCB | TRUE | high | faulty main control board | control_board | FALSE | TRUE | Other | na | EODA18H-2436 | EODA18H | 1.5 |  | 2022-07-25 | 2026-01-27 | 1282 | >2y | outdoor condenser not turning on with 24 volts at the board between Y and common | The technician, Spencer, reported that the electric heat strip on the Eco air handler was not functioning, with no amperage detected and only cold air blowing. Mauricio confirmed that the thermostat was set to heating and guided Spencer to check the settings on the outdoor unit and the thermostat. Spencer provided the last six digits of the unit's serial number (1044826) for reference. Mauricio instructed Spencer to check the voltage between the yellow wire and common, confirming 24 volts was present, indicating the thermostat was calling for heat. Spencer was advised to check the voltage at the outdoor unit and to ensure the common wire was intact, as a previous issue had been reported with it being broken. After confirming voltage readings, Mauricio suggested resetting the unit and checking the voltage between the O and common wires, which showed 10 volts, indicating a potential issue with the heating call. Mauricio explained that the board was likely protecting itself due to the unexpected voltage readings and instructed Spencer to remove the O wire and test the system again. Spencer confirmed that both thermostats were calling for heat, and Mauricio advised checking the voltage again after the reset. Mauricio agreed to send Spencer a part number for the board and confirmed that Spencer could contact their supply house for the part. Tasks Mauricio will send Spencer a part number for the board needed for the Eco air handler. Mauricio will create a ticket number and send it to Spencer's phone (5086177429). |  | EODA18H-2436 | EAHATN-36 | na | 1L754WL500ZL51700034 |  | EAC230904173
23649 | 2026-01-28 | 2026 | 1 | 2026-01 | Drain Pan | TRUE | medium | cracked drain pan | drain_water | FALSE | TRUE | Other | na | EODA18H-2436 | EODA18H | 1.5 |  | 2021-05-26 | 2026-01-27 | 1707 | >2y | Cracked Drain Pan | Per email: Cracked Drain Pan |  | EODA18H-2436 | EAHATN-36 | . | F52290000100HA100107 | Drain Pan 1 | EAC230701545
23651 | 2026-01-28 | 2026 | 1 | 2026-01 | MCB | TRUE | high | shorted control board | control_board | FALSE | TRUE | Other | na | EODA 18H 2436 | EODA | 1.5 |  |  | 2026-01-27 |  | unknown | bad board with surge protector installed | Jacob Pereira reported a problem with a unit, indicating that the control board is dead with a burn mark, suggesting it may be shorted out. Mauricio Cordeiro requested pictures of the unit, including the EMI filter, control board, and measurements of the compressor wires, to assist in diagnosing the issue. Jacob Pereira confirmed that he checked the compressor wires and will verify the ohm readings, which he initially believed to be 40. Mauricio Cordeiro advised Jacob to ensure the compressor is not faulty and to take pictures of all measurements and the model number of the unit for ticket creation. Jacob Pereira confirmed the job location is in South Dartmouth and will contact the Portland group to check for a needed part, while also noting that Mauricio has a part available at his house if necessary. Tasks Jacob Pereira will take pictures of the unit, including the EMI filter, control board, and compressor wire measurements, and send them to Mauricio Cordeiro within 15 minutes. Jacob Pereira will verify the ohm readings of the compressor wires and report back to Mauricio Cordeiro. Jacob Pereira will contact the Portland group to check for a required part for the unit. |  | EODA 18H 2436 | na | na | 16015WK415ZK71700059 | MCB | EAC230904173
23654 | 2026-01-28 | 2026 | 1 | 2026-01 | MCB | TRUE | high | voltage fluctuation damage | control_board | FALSE | TRUE | Refrigerant Circuit | c3 | EODA18H-2436 | EODA18H | 1.5 |  |  |  |  | unknown | bad board at condenser with surge protector installed | The technician reported a C3 error on an Eco unit, indicating voltage issues, and described the current suction pressure as 63 and head pressure as 365. Mauricio Cordeiro suggested that the technician obtain a Gateway device to facilitate easier diagnostics and monitoring of the unit. The technician confirmed the unit is approximately one year old, with the model number EODA18H-24, and discussed the need for a specialized Gateway for their toolkit. Voltage readings were taken, showing 245 volts, which is within acceptable limits, but the technician was advised to monitor for fluctuations. The technician was instructed to check the compressor's wiring and measure the ohms between the wires to ensure proper functionality. After troubleshooting, the technician was advised to let the unit run for 10-15 minutes and check for any error codes or pressure readings afterward. Mauricio Cordeiro indicated that if the C3 error persists, the technician may need to consider replacing the control board, pending further voltage checks. Tasks The technician is to obtain a Gateway device from their sales representative for easier diagnostics. The technician is to check the voltage after running the unit for 10-15 minutes and report back if any issues persist. The technician is to measure the ohms between the compressor wires and check for continuity |  | EODA18H-2436 | na | na | 166I5WQ500ZQ50800037 | None;MCB | EAC230904173
23656 | 2026-01-28 | 2026 | 1 | 2026-01 | MCB | TRUE | high | EEPROM parameter error | communication | FALSE | TRUE | Control Board | E0 | EODA19H-2436AAA | EODA19H | 2 |  | 2025-09-17 |  |  | unknown | E0 Error | E0 Error |  | EODA19H-2436AAA | . | . | 0EWH003385Z247160001 | MCB | EAC230904173
23698 | 2026-01-28 | 2026 | 1 | 2026-01 | Leakage | TRUE | high | indoor coil leak | refrigerant | FALSE | TRUE | Other | na | na | NA |  |  |  | 2026-01-28 |  | unknown | coil leak at indoor unit | coil leak at indoor unit |  | na | EAHATN_36 | na | na | Evaporator assembly | EAC1099000008
23699 | 2026-01-29 | 2026 | 1 | 2026-01 | MCB | TRUE | high | electrical surge damage | control_board | FALSE | TRUE | Protection | P1 | EODA18H-2436 | EODA18H | 1.5 |  |  | 2026-01-28 |  | unknown | No surge protector, bad board and high pressure sensor | No surge protector, bad board and high pressure sensor |  | EODA18H-2436 | . | . | 1W123WM300ZM30700808 | MCB;Other | EAC230904173 & 231235159
23704 | 2026-01-29 | 2026 | 1 | 2026-01 | Motor | TRUE | high | inducer motor failure | mechanical | FALSE | TRUE | Control Board | E2 | . | . |  |  | 2026-01-28 | 2026-01-28 | 0 | ≤30d (infant) | E2 Error, inducer motor not working properly | E2 Error, inducer motor not working properly. | E2 | . | . | MGH96M100C5A | . | Other | 17400801000935
23707 | 2026-01-29 | 2026 | 1 | 2026-01 | MCB | TRUE | high | failed main control board | control_board | FALSE | TRUE | Other | blank display | EODA18H-4860 | EODA18H | 1.5 |  |  | 2026-01-28 |  | unknown | Blank display | Blank display. Ohm reading is good. |  | EODA18H-4860 | . | . | 10608WL900ZL92600004 | MCB | EAC230904171
23742 | 2026-01-30 | 2026 | 1 | 2026-01 | MCB | TRUE | high | damaged inverter board | control_board | FALSE | TRUE | Refrigerant Circuit | C9 | EODA18H-2436 | EODA18H | 1.5 |  | 2023-03-15 | 2026-01-29 | 1051 | >2y | Unit has bad inverted. Recommending MCB replacement. Please credit TPG Raynham | Error Code: C9 Diagnosis: Damaged Inverter, replace board. Test: Compressor, ohm: U-W 1.0 V-U 1.4 V-W 1.0 Inverter board: B -U .47 v R- U OL B -V .47 v R-V OL B -W .45 v R-W OL |  | EODA18H-2436 |  |  | 1a521wm400zm41900994 | None;MCB | EAC230904165
23751 | 2026-01-30 | 2026 | 1 | 2026-01 | Gas Furnace | TRUE | high | defective gas valve board | control_board | FALSE | TRUE | Control Board | E8/E7 | na | NA |  |  | 2026-01-29 | 2026-01-29 | 0 | ≤30d (infant) | new install bad gas valve and furnace board | The technician confirmed that the NL error message does not affect the furnace's operation, as it can still function despite the error. The technician guided the caller through checking the thermostat wiring and confirmed that the thermostat was set up correctly for heating mode. The technician advised the caller to check the gas pressure, indicating that it should be between 4.5 to 10 inches of water column for proper operation. The technician identified that the E7 error code indicated an ignition failure and instructed the caller to disconnect and reconnect wires to reset the system. The technician confirmed that the gas valve was not opening despite receiving the correct voltage, suggesting a faulty gas valve as the likely cause of the issue. The technician discussed the need for a dual fuel kit for the heat pump and confirmed that the caller's furnace was not functioning properly due to gas pressure issues. The technician offered to assist in locating replacement parts for the gas valve and control board, emphasizing the urgency of the situation due to the cold weather conditions. Tasks The technician will locate the necessary parts for the gas valve and control board and expedite the order to the caller's supply house. The caller is to send a picture of the model number and data tag for the furnace to assist in the parts order. The technician advised the caller to monitor the furnace's operation after making adjustments to the gas pressure and to check for any further error codes. |  | na | na | MGH96M1205A | na | Gas valve;AHU Motherboard | EAC17427600001389 /EAC17127600000708
23758 | 2026-01-30 | 2026 | 1 | 2026-01 | Leakage | TRUE | high | cased coil refrigerant leak | refrigerant | FALSE | TRUE | Communication | H0 | . | . |  |  | 2025-04-24 | 2026-01-30 | 281 | 31-365d | Cased Coil leak via email | per joshua, Cased Coil leak via email getting coil from colbalt |  | . | GNC3036BPT | . | . | Evaporator assembly | GNC3036BPT
23761 | 2026-01-31 | 2026 | 1 | 2026-01 | MCB | TRUE | medium | sensor or board fault | control_board | FALSE | TRUE | Refrigerant Circuit | C4 | EODA18H-4860 | EODA18H | 1.5 |  | 2026-01-30 | 2026-01-30 | 0 | ≤30d (infant) | C4 Error | C4 Error |  | EODA18H-4860 | . | . | 1O608WL800ZL81600639 | MCB;Compressor | EAC230904171, 231235532
23803 | 2026-02-02 | 2026 | 2 | 2026-02 | Top Cover | TRUE | medium | ice accumulation damage | other | FALSE | TRUE | Other | na | EODA18H-2436 | EODA18H | 1.5 |  | 2022-07-22 | 2026-01-31 | 1289 | >2y | condenser top assembly broken | Homeowner sent pictures of the condenser top assembly broken due to ice accumulation . . |  | EODA18H-2436 | EAHATN-36 | na | 1O372WL800ZL80300244 |  | 230803000
23804 | 2026-02-02 | 2026 | 2 | 2026-02 | MCB | TRUE | high | control board fire failure | control_board | FALSE | TRUE | Protection | PC40 | ESCA16H-36 | ESCA16H | 3 |  |  |  |  | unknown | PC40 Error board cuaght on fire | PC40 Error board cuaght on fire |  | ESCA16H-36 | . | . | 3EWH001950Z234050058 | MCB | ESCA16H-36
23805 | 2026-02-02 | 2026 | 2 | 2026-02 | Top Cover | TRUE | low | broken top cover | cosmetic | FALSE | TRUE | Other | na | EODA18H4860 | EODA18H | 1.5 |  |  | 2026-02-02 |  | unknown | broken top assembly | home onwer called to report a broken top assembly on her condenser . |  | EODA18H4860 | na | na | 10608WL900ZL92600132 |  | 230803000
23807 | 2026-02-02 | 2026 | 2 | 2026-02 | MCB | TRUE | high | main control board failure | control_board | FALSE | TRUE | Other | na | EODA18H-4860 | EODA18H | 1.5 |  | 2023-06-28 | 2026-02-02 | 950 | >2y | bad board on outside condenser | The main issue discussed was a dead board on an EODA 18H unit in Dennis, Cape Cod, which was the only source of heat for the building. The technician reported that power was coming in, but nothing was active on the board. The technician provided the last six digits of the gateway's serial number, which was 30000445, confirming the presence of a C3 alert and other alerts on the system. The technician reported low voltage readings of 230 volts coming into the transformer and 235 volts coming out, which were deemed insufficient for the system's operation. The technician was instructed to take voltage readings from L1 and L2 on the board and send pictures of the readings, the blank board, and the surge protector to assist in diagnosing the issue. The technician was advised to shut off the unit and remove the compressor wires for further inspection, ensuring safety precautions were taken during the process. The technician was reminded to check the grounding of the compressor and to send a picture of the readings to facilitate the creation of a warranty ticket for the old board once it was returned. Tasks The technician is to take voltage readings from L1 and L2 on the board and send pictures of the readings, the blank board, and the surge protector to Mauricio. The technician is to shut off the unit and remove the compressor wires for inspection. The technician is to contact Webs for immediate assistance with the part needed for the system. |  | EODA18H-4860 | GNC4860DPT | na | 1W967WM400ZM40100355 |  | EAC230904171
23819 | 2026-02-03 | 2026 | 2 | 2026-02 | MCB | TRUE | high | main control board failure | control_board | FALSE | TRUE | Other | na | EODA18H4860 | EODA18H | 1.5 |  |  |  |  | unknown | bad board on outdoor condenser | The Tech Support representative reported a problem with the main board of the Hip Hop system, indicating it was broken and required replacement. Mauricio Cordeiro confirmed that the board was not receiving the correct voltage and requested a picture of the voltage reading between L1 and L2 to assess the issue further. Mauricio provided the part number E2309041 for the replacement board and explained the need for the homeowner's complete information to facilitate shipping, including the contractor's name, address, and email. The Tech Support representative confirmed that the homeowner would measure the voltage and send a picture of the meter reading to Mauricio. Mauricio emphasized the importance of installing a surge protector to prevent future issues and requested a picture of the installed surge protector once it was in place. Tasks The Tech Support representative is to send a picture of the voltage reading from the main board to Mauricio. The Tech Support representative is to gather and send the homeowner's complete information, including the contractor's name, address, and email, to Mauricio. The Tech Support representative is to ensure that a surge protector is installed and send a picture of it to Mauricio after installation. |  | EODA18H4860 | na | na | 10608WL900ZL92600039 | MCB | EAC230904171
23823 | 2026-02-03 | 2026 | 2 | 2026-02 | MCB | TRUE | high | burnt control board | control_board | FALSE | TRUE | Other | blank screen | EODA18H-2436 | EODA18H | 1.5 |  |  |  |  | unknown | Burnt control board. System has surge protector installed | Burnt control board. System has surge protector installed |  | EODA18H-2436 | . | . | 1A521WM700ZM71402041 | MCB | EAC230904173
23827 | 2026-02-03 | 2026 | 2 | 2026-02 | Top Cover | TRUE | medium | damaged fan blade | mechanical | FALSE | TRUE | Other | na | EDDA18H-2436 | EDDA18H | 1.5 |  |  |  |  | unknown | broken top assembly, bent fan blade | broken top assembly, bent fan blade |  | EDDA18H-2436 | na | na | 10372WL800ZL80300115 | Other | 230803000
23829 | 2026-02-03 | 2026 | 2 | 2026-02 | E-code | TRUE | high | indoor outdoor communication error | communication | FALSE | TRUE | Control Board | E0 | EODA18H-4860 | EODA18H | 1.5 |  |  |  |  | unknown | E0 Error | E0 Error | E0 | EODA18H-4860 |  |  | 1W967WM700ZM71700470 | MCB | EODA18H-2436BAA
23842 | 2026-02-03 | 2026 | 2 | 2026-02 | MCB | TRUE | high | faulty board and sensor | control_board | FALSE | TRUE | Other | na | EODA19H-2436AAA | EODA19H | 2 |  | 2025-10-23 |  |  | unknown | Faulty board and TA sensor | Faulty board and TA sensor, MCB will not output 24 to W wire. |  | EODA19H-2436AAA | EAHAEC-36 | . | 0EWH003250Z244260005 | MCB | EAC17123000011324 (2/10/26), EAC17122000059682 (2/10/26), EAC230904173 & EAC2309100005
23846 | 2026-02-04 | 2026 | 2 | 2026-02 | Leakage | TRUE | high | indoor coil refrigerant leak | refrigerant | FALSE | TRUE | Other | S3/S1/H0 | EODA18H-2436 | EODA18H | 1.5 |  | 2023-10-04 | 2026-02-02 | 852 | >2y | coil leak at indoor unit | Tech Support - QUATTRUCCI N. requested to switch service for a homeowner from another company, but Mauricio Cordeiro indicated that this could not be done over the phone and offered to gather necessary information instead. Mauricio Cordeiro advised Tech Support - QUATTRUCCI N. to send a picture of the Gateway for further assistance and confirmed that the unit had been shut down due to prior issues. During the call, Mauricio Cordeiro identified a severe alarm indicating a refrigerant leak and noted that the unit had not been operational since January 3rd, which was confirmed by Tech Support - QUATTRUCCI N. Mauricio Cordeiro suggested conducting a pressure test to confirm the leak and offered to provide a part number and case number for warranty purposes once the issue was confirmed. They discussed the importance of changing the filter when dealing with coil issues to prevent humidity from affecting the system, and Mauricio Cordeiro confirmed that the part was under warranty, facilitating the repair process. Tasks Tech Support - QUATTRUCCI N. will text Mauricio Cordeiro with the company's information and a picture of the Gateway. Tech Support - QUATTRUCCI N. will talk to the homeowner to confirm the timeline of the issues, particularly regarding the January 3rd date. Mauricio Cordeiro will provide a part number and case number for warranty once the leak is confirmed. |  | EODA18H-2436 | EAHATN-36 | na | 1O372WL800ZL80300023 | Evaporator assembly | EAC1099000008
23851 | 2026-02-04 | 2026 | 2 | 2026-02 | Top Cover | TRUE | high | fan assembly failure | mechanical | FALSE | TRUE | Other | na | EODA18H2436 | EODA18H | 1.5 |  |  | 2026-02-03 |  | unknown | broken top assembly on condenser | The technician, Larry Jackson, reported that the fan of the ecore condenser unit broke off, causing damage to the coil. Mauricio Cordeiro requested pictures of the unit to assess the damage and determine the next steps. Mauricio instructed Larry to take a picture of the entire condenser in relation to the house and send it over for further evaluation. They discussed the need for a part number and the location of the job, which is in Deerfield, Massachusetts, at 105 Pine Nook Road. Larry confirmed that they would attempt to replace the entire unit due to additional damage to the piping, and Mauricio explained that the top assembly comes as a single piece. Mauricio emphasized the importance of protecting the unit with a cover to prevent future damage from snow, noting that this was the third incident in Massachusetts. They agreed that if the coil has a leak, it would require a different approach, and Larry planned to check with the technician who was previously on-site to confirm the status of the coil. Mauricio stated he would send the pictures to his boss for further action and indicated he would call back in about 10 minutes to follow up. Tasks Larry Jackson is to send pictures of the condenser unit to Mauricio for assessment. Larry will check with the technician who was previously on-site regarding the coil's status and potential leaks. Mauricio will send the pictures to their boss for further evaluation and decision-making. |  | EODA18H2436 | na | na | 10372WL800ZL8030015 | Other | EODA18H2436
23853 | 2026-02-04 | 2026 | 2 | 2026-02 | Leakage | TRUE | high | evaporator coil leak | refrigerant | FALSE | TRUE | Other | none | none | NONE |  |  | 2025-11-20 |  |  | unknown | Evap Coil | The evaporator coil is leaking. |  | none | eahatn-24 | na | none | Other | eac1099000008
23867 | 2026-02-04 | 2026 | 2 | 2026-02 | TXV | TRUE | medium | blocked TXV valve | refrigerant | FALSE | TRUE | Other | na | na | NA |  |  |  | 2026-02-03 |  | unknown | bad TXV at air handler | Tech Support - Rezende Kevin reported suction pressure at 96 and liquid pressure at 280, with temperatures indicating a heating issue. Mauricio Cordeiro guided them through diagnostics, confirming low compressor speed and potential freon issues. Mauricio instructed Tech Support - Rezende Kevin to check model numbers and error codes, leading to the identification of a P7 error indicating pressure issues. They discussed the importance of having an app for easier diagnostics. After further diagnostics, it was determined that the TXV might be blocked, causing low temperature differentials and insufficient heating. Mauricio recommended replacing the TXV and provided a part number for ordering. Mauricio emphasized the need for a secondary heat source, such as an electric backup, to ensure adequate heating during extreme cold, advising Tech Support - Rezende Kevin to communicate this to the customer. Tasks Tech Support - Rezende Kevin is to send a picture of the model number of the air handler to Mauricio for record-keeping. Tech Support - Rezende Kevin is to contact the Portland group to order the TXV part using the provided part number. Tech Support - Rezende Kevin is to discuss the need for a secondary heat source with the customer and provide recommendations for electric backup heating. |  | na | EAHATN-60BAA | na | na | TXV | E.AC.231235631
23880 | 2026-02-05 | 2026 | 2 | 2026-02 | Motor | TRUE | high | defective blower motor | electrical | FALSE | TRUE | Other | 0 | 0 | 0 |  |  | 2022-06-22 | 2026-02-02 | 1321 | >2y | Blower defective - GV2829 | *Replacement of the blower motor Upon arrival at the residence, it was observed that the air handler located on the third floor was not operating and there was no airflow in the system. After inspection and electrical testing, it was determined that the blower motor is defective and not engaging. In order for the system to operate properly, replacement of the blower motor with a new compatible unit is required. |  | 0 | EAHATN-36 | 0 | 0 | None;Fan Motor | Fan motor
23891 | 2026-02-05 | 2026 | 2 | 2026-02 | MCB | TRUE | high | shorted main control board | control_board | FALSE | TRUE | Other | na | EODA18H-4860 | EODA18H | 1.5 |  | 2024-04-28 | 2026-02-05 | 648 | 1-2y | bad board at condenser with surge protector installed | Mauricio and the caller discussed the electrical issues at the job site related to a homeowner named Frank, who had a high electric bill due to equipment malfunction. They identified that the board needed replacement due to shorts. The caller confirmed they had taken pictures of the board and other relevant equipment, which they agreed to send to Mauricio for further assessment. Mauricio provided the part number needed for the replacement board and explained the warranty process, clarifying that the caller would need to purchase the part from a supply house and provided a ticket number for warranty reference. They discussed the need for the caller to check the voltage going into the house and to adjust the new board according to the instructions that would come with it, emphasizing the importance of these steps for proper functionality. Tasks The caller is to send Mauricio pictures of the board and other relevant equipment. Mauricio will create a ticket number for the warranty and send the part number to the caller. The caller is to check the voltage going into the house and send Mauricio a picture of the meter reading. |  | EODA18H-4860 | EAHATN-60 | na | 1A681WM400ZM40100157 | MCB | ESAC230904171
23892 | 2026-02-05 | 2026 | 2 | 2026-02 | Leakage | TRUE | high | evaporator coil leak | refrigerant | FALSE | TRUE | unknown |  | EAHATN-48 | EAHATN | 4 |  |  |  |  | unknown | COIL LEAK | COIL LEAK |  |  | EAHATN-48 | . |  | Evaporator Only | EAC1099000009
23894 | 2026-02-06 | 2026 | 2 | 2026-02 | Leakage | TRUE | high | indoor coil leak | refrigerant | FALSE | TRUE | Other | na | na | NA |  |  |  | 2026-02-05 |  | unknown | coil leak at air handler | Chris (Revise) initiated the call to request a ticket number for an E-Core indoor coil under warranty. Mauricio Cordeiro (Customer Support Representative) recognized Chris and acknowledged the increased calls due to the cold snap affecting many customers. Chris mentioned he prefers Ecoer's systems over others, indicating a positive sentiment towards the brand. Mauricio requested Chris to send a picture of the coil's serial number to proceed with the ticket creation. The conversation included technical discussions about leak detection and troubleshooting methods, showcasing Chris's expertise. Mauricio provided Chris with the part number for the coil and assured him he would send a ticket number shortly. Chris expressed appreciation for Mauricio's assistance, highlighting a positive customer service experience. The conversation began with Chris from Revise calling Mauricio Cordeiro, a Customer Support Representative, to request a ticket number for an E-Core indoor coil that is under warranty.Mauricio quickly recognized Chris and they discussed the increased volume of calls due to the cold weather. Chris shared his preference for Ecoer's systems, while Mauricio guided him to send a photo of the coil's serial number.Their technical discussion about leak detection methods revealed both parties' expertise. Mauricio provided the necessary part number and assured Chris that he would send the ticket number promptly.The call ended with Chris expressing gratitude for the assistance provided. |  | na | EAHATN36BAA | na | na | Evaporator assembly | EAC1099000008
23947 | 2026-02-06 | 2026 | 2 | 2026-02 | MCB | TRUE | high | dead control board | control_board | FALSE | TRUE | Other | No display | EODA18H-2436 | EODA18H | 1.5 |  | 2023-02-17 | 2026-01-16 | 1064 | >2y | NEW MCB Unit had no display on board | Wholesaler reached out to us. They dealt with a contractor who had a system that had not heat. Unit had no display on board. Contractor showed up with a replacement board. The brand-new replacement board they got from the wholesaler had the same issue. They then took another board that the wholesaler had and that 2nd board worked. The wholesaler is looking for credit for QTY 2 of 230904156. They have the old boards. If you would like them back for testing, please let me know and I can coordinate. Please credit FW Webb Springfield VT for QTY 2 of 230904156 |  | EODA18H-2436 |  |  | 1A521WM400ZM42401357 | MCB | 230904156
23950 | 2026-02-07 | 2026 | 2 | 2026-02 | MCB | TRUE | high | faulty main control board | control_board | FALSE | TRUE | unknown | [8 empty] | unknown | RGA Request | We have a bad board. Case# 23194 | [6 empty] | eoda18h2436baa
23956 | 2026-02-07 | 2026 | 2 | 2026-02 | Leakage | TRUE | high | indoor coil leak | refrigerant | FALSE | TRUE | Other | na | EODA18H-4860 | EODA18H | 1.5 |  | 2022-09-01 |  |  | unknown | Coil leak | Coil leak |  | EODA18H-4860 | EAHATN-48 | . | 1O608WL800ZL81600480 | Evaporator assembly | EAC230904171(02/11/26), EAC2323100001(02/11/26), EAC1099000009
23984 | 2026-02-09 | 2026 | 2 | 2026-02 | Leakage | TRUE | high | indoor coil leak | refrigerant | FALSE | TRUE | Other | na | EODA18H-4860 | EODA18H | 1.5 |  | 2024-06-04 |  |  | unknown | Coil Leak | Per email from johnstone Coil Leak |  | EODA18H-4860 | EAHATN-48 | . | 1M510WL600ZL61800086 | Evaporator Only | EAC1099000009
23985 | 2026-02-09 | 2026 | 2 | 2026-02 | MCB | TRUE | high | faulty main control board | control_board | FALSE | TRUE | Control Board | E0/C2/C9/C3 | EODA18H-4860BAA | EODA18H | 1.5 |  | 2025-03-21 | 2026-02-09 | 325 | 31-365d | bad board at condenser with surge protector | The technician confirmed the issue with the unit that was tripping and began troubleshooting by asking for voltage readings and wire checks. The technician instructed the support person to take voltage measurements, which revealed a low voltage of 229 volts, indicating a potential problem. The technician guided the support person through checking the ohm readings between wires, which returned acceptable values, suggesting the compressor was functioning properly. The technician concluded that the board was likely faulty based on the readings and provided a part number (EAC 30904171) for the support person to order from their usual supplier, SW Web. The technician advised the support person to take pictures of the voltage readings, ohm readings, and the surge protector for documentation and warranty purposes, and promised to create a ticket number for the warranty claim. Tasks The support person is to take pictures of the voltage readings, ohm readings, and the surge protector and send them to the technician. The support person is to call SW Web to order the replacement board using the provided part number. |  | EODA18H-4860BAA | 167TXWQ500ZQ51200061 | na | 167TXWQ500ZQ51200061 | MCB;Compressor | EAC230904171 /EAC231235532
23986 | 2026-02-09 | 2026 | 2 | 2026-02 | MCB | TRUE | high | high voltage surge damage | control_board | FALSE | TRUE | Control Board | Eo/C9/C3/C2 | EODA18H4860 | EODA18H | 1.5 |  |  |  |  | unknown | bad board on the outdoor condenser | The caller confirmed they arrived at the location and discussed the Gateway model number 7001205, which was previously replaced, indicating a lack of records for the unit. Voltage readings were taken, showing 247 volts going into the system, with concerns raised about high voltage levels in Massachusetts potentially damaging equipment. The technician advised the caller to take pictures of the model and serial numbers of the condensing unit and surge protector for records. The technician instructed the caller to shut off the unit and check the compressor wires for voltage readings, noting that previous readings indicated potential compressor issues. The technician provided a part number (2309041) for the replacement board and instructed the caller to contact the Portland Group for procurement, emphasizing the importance of following installation instructions upon receipt of the new board. The technician offered to create a warranty ticket for the caller, requesting their name and company information to facilitate the process. Tasks The caller is to take pictures of the model and serial numbers of the condensing unit and surge protector and send them to the technician. The caller is to contact the Portland Group to obtain the replacement board using the provided part number 2309041. The caller is to send their name and company information to the technician to create a warranty ticket. |  | EODA18H4860 | na | na | 1A681WM600ZM60500509 |  | EAC230904171
24011 | 2026-02-10 | 2026 | 2 | 2026-02 | EMI | TRUE | high | burnt EMI filter | electrical | FALSE | TRUE | Other | na | EODA18H-4860 | EODA18H | 1.5 |  | 2020-11-20 |  |  | unknown | Burnt EMI filter | Burnt EMI filter |  | EODA18H-4860 | . | . | 16015WK417ZK60300010 | EMi Filter | 230904303, 230904304, 230904159
24015 | 2026-02-11 | 2026 | 2 | 2026-02 | MCB | TRUE | high | faulty main control board | control_board | FALSE | TRUE | Other | na | EODA18H-2436 | EODA18H | 1.5 |  |  |  |  | unknown | Per Joshua, Send MCB to Fasco | Per Joshua, Send MCB to Fasco |  | EODA18H-2436 | . | . | 1A521WM400ZM42401448 | MCB | EAC230904173
24022 | 2026-02-11 | 2026 | 2 | 2026-02 | Leakage | TRUE | high | refrigerant leak at coil | refrigerant | FALSE | TRUE | Other | 0 | 0 | 0 |  |  | 2022-04-05 | 2026-02-05 | 1402 | >2y | Leak Coill | REPORT 1. Condition Found The visit was performed to search for refrigerant leaks in the second floor unit due to repeated heating performance problems. 2. Diagnosis Performed After performing leak inspection procedures, the following conditions were identified: Leak detector dye marks were found on the coil. Significant oil residue was observed on multiple areas around the coil. The findings indicate an active refrigerant leak at the coil. 3. Actions Performed Leak inspection was completed on the second floor unit. Refrigerant charge was adjusted as needed to allow the system to continue operating in heating mode temporarily. System operation was verified after charge adjustment. 4. Technical Assessment The coil is leaking and must be replaced to permanently resolve the heating issue. Current operation is temporary and dependent on the adjusted refrigerant charge. |  | 0 | EAHATN-60 | 0 | 0 | None;Evaporator assembly | 0
24033 | 2026-02-11 | 2026 | 2 | 2026-02 | Leakage | TRUE | high | indoor coil leak | refrigerant | FALSE | TRUE | Other | na | na | NA |  |  |  | 2026-02-10 |  | unknown | coil leak at air handler | Roache Steven reported a leak in a brand new air handler unit, stating that the coil is leaking nitrogen. Mauricio Cordeiro requested pictures of the leak to assess the situation further. Roache Steven confirmed that the air handler unit was installed in June 2025 and that he had recently connected the condenser, but upon testing, found no nitrogen in the system, indicating a leak. Mauricio Cordeiro acknowledged the issue and asked Roache Steven to send the pictures to his phone number, 571-491-8318, for further action. Tasks Roache Steven will send pictures and a video of the leaking air handler unit to Mauricio Cordeiro's phone number, 571-491-8318. Mauricio Cordeiro will provide a part number and further assistance once he receives the picture |  | na | EAHATN48 | na | na | Evaporator assembly | EAC1099000009
24036 | 2026-02-11 | 2026 | 2 | 2026-02 | Leakage | TRUE | high | brazed joint leak | refrigerant | FALSE | TRUE | Other | na | EODA19H-2436AAA | EODA19H | 2 |  | 2025-05-29 |  |  | unknown | condenser coil leak | Diagnosed a total refrigerant loss due to a leak in the outdoor coil on a factory brazed joint for the sensor well on the coil U Bend. We also had defective Schrader cores that we replaced because we couldn’t pull a proper vacuum on the entire system. |  | EODA19H-2436AAA | . | . | 0EWH003128Z243130036 | Other | Condenser Coil
24040 | 2026-02-12 | 2026 | 2 | 2026-02 | Leakage | TRUE | high | indoor coil leak | refrigerant | FALSE | TRUE | Other | na | na | NA |  |  |  | 2026-02-10 |  | unknown | coil leak at air handler | The technician from New Brunswick, calling from a dissolved installation company, reported a leak in the indoor coil of a two-year-old Ecoair central unit and requested a replacement part. Mauricio confirmed that the technician's company is registered with the Canadian government (CRN) and has a bond with CBSA, ensuring warranty eligibility and no issues with customs or shipping. The technician will send Mauricio via text message the company's name, address, contact information, and photos of the leak, as well as the model and serial numbers of the unit. Mauricio will create a ticket number and arrange for the shipment of the replacement coil under warranty, with no shipping charges expected. The technician will also send Mauricio the order form and relevant unit information, and Mauricio will coordinate the process accordingly. Tasks The technician from FREDERICTON NB will text Mauricio at 571-491-8318 with their company's name, address, contact details, and photos of the leaking coil, as well as the model and serial numbers of the unit. Mauricio will generate a ticket number and arrange for the shipment of the warranty replacement coil once he receives the necessary information and images from the technician. |  | na | EAHATN-36, | na | na | Evaporator assembly | EAC1099000008
24042 | 2026-02-12 | 2026 | 2 | 2026-02 | Leakage | TRUE | high | indoor coil leak | refrigerant | FALSE | TRUE | Other | na | na | NA |  |  |  | 2026-02-09 |  | unknown | coil leak at indoor unit | coil is leaking at indoor unit |  | na | EAHATN 60 | na | na | Evaporator assembly | EAC1099000009
24046 | 2026-02-12 | 2026 | 2 | 2026-02 | Leakage | TRUE | high | refrigerant leak | refrigerant | FALSE | TRUE | Other | oil in pan | EODA18H-2436 | EODA18H | 1.5 |  | 2023-08-17 | 2026-02-01 | 899 | >2y | Please ship asap | Please ship asap. Thank you |  | EODA18H-2436 | EAHATN-24 |  | 1A521WM700ZM70301743 | Evaporator Only | Evaporator Coil
24048 | 2026-02-12 | 2026 | 2 | 2026-02 | Leakage | TRUE | high | refrigerant leak | refrigerant | FALSE | TRUE | Compressor | leak detected | EODA18H-2436 | EODA18H | 1.5 |  | 2022-05-16 | 2026-02-05 | 1361 | >2y | please ship asap | please ship asap |  | EODA18H-2436 | EAHATN-36 |  | 1W123WM100ZM11600269 | Evaporator Only | Evaporator Coil
24125 | 2026-02-17 | 2026 | 2 | 2026-02 | MCB | TRUE | high | shorted motor and board | control_board | FALSE | TRUE | Other | Burnt board. No code | EAHATN-36 | EAHATN | 3 |  | 2024-09-27 | 2026-02-16 | 507 | 1-2y | New Motor and Fan Delay Kit | Issue 1: Indoor motor will not run. Strong electrical smell from motor. Diagnosis Checked incoming voltage 126 volts Output voltage from board 0 Volts Recommendation: Replace indoor fan motor and Main Control Board |  |  | EAHATN-36 |  |  | None;MCB | 230904148 & 36K-FLF001
24126 | 2026-02-17 | 2026 | 2 | 2026-02 | MCB | TRUE | high | grounded compressor | mechanical | FALSE | TRUE | Refrigerant Circuit | CC Code | EODA18H-2436 | EODA18H | 1.5 |  | 2022-08-12 | 2026-02-16 | 1284 | >2y | Please credit Thames Valley for 230905165 & 231235530 | Issue 1: Outdoor Heat pump will not start . CC Code Diagnosis Checked incoming voltage 244 volts into EMI Filter, 244 out of EMI Filter Ohm Compressor, U-V 0.8 V-W 0.8 W-U 0.8 Winding to ground U 1.5 V 1.9 W 1.9 Comptessor appears to be grounded. Recommendation: Replace Compressor and MCB |  | EODA18H-2436 |  |  | 1W123WM200ZM20500544 | None;MCB;Compressor | 230905165 & 231235530
24141 | 2026-02-18 | 2026 | 2 | 2026-02 | MCB | TRUE | high | faulty control board | control_board | FALSE | TRUE | Other | na | EODA18H4860 | EODA18H | 1.5 |  | 2027-08-27 | 2026-02-15 |  | unknown | bad board and EMI filter | Tech Support from ADKINS IRA contacted Mauricio Cordeiro to inquire about purchasing parts for an e-core unit, specifically a noise filter and a board. Mauricio Cordeiro confirmed understanding of the request and asked for further details to assist in locating the parts. The Tech Support representative initially hesitated and then indicated they would provide more information, but ultimately did not specify where to buy the parts during the call. |  | EODA18H4860 | na | na | 16015WK417ZK60300138 |  | EAC230904159/EAC230904171
24148 | 2026-02-18 | 2026 | 2 | 2026-02 | EMI | TRUE | high | bad EMI filter | electrical | FALSE | TRUE | Other | na | EODA18H-4860 | EODA18H | 1.5 |  | 2020-11-20 | 2026-02-17 | 1915 | >2y | bad EMI filter by Joshua | bad EMI filter |  | EODA18H-4860 | EAHATN-36 | na | 16015WK417ZK60300010 | EMi Filter | EAC230904159
24158 | 2026-02-18 | 2026 | 2 | 2026-02 | MCB | TRUE | high | control board failure | control_board | FALSE | TRUE | Control Board | E0/C1/C0 | EODA18H2436BAA | EODA18H | 1.5 |  |  | 2026-02-18 |  | unknown | bad board on outdoor unit with surge protector | Spencer reported an E0 system lockout on an Eco unit located in Westport 7, Meadow Brooklyn, with no Gateway installed, and confirmed the absence of a Gateway on the unit. Mauricio asked for voltage readings before and after the EMI filter, which Spencer provided as approximately 245.7V before and 245.9V after, indicating stable voltage levels. Error codes 23 (E0), 24 (C1), and 25 (C0) were retrieved, with E0 confirmed as the primary issue, likely caused by voltage irregularities or control board failure. Mauricio instructed Spencer to shut off the unit, disconnect wires from the second compressor, and perform grounding checks, which appeared satisfactory. Voltage measurements on the compressor wires were 1.2 ohms, indicating no grounding issues, and Mauricio advised reassembling the unit and testing for reset. They discussed high voltage issues in the neighborhood, with Mauricio noting that voltages exceeding standard ratings can damage equipment, especially with solar installations increasing voltage levels. Mauricio identified the unit as model EODA18H-2436B-AA, second generation, and determined a new control board is needed, providing a part number and suggesting procurement from local suppliers like Portland Group or FW Webb. Mauricio arranged for Spencer to send pictures of the unit, serial number, and voltage readings, and promised to generate a warranty ticket once the parts are received and the old board is returned. Tasks Spencer from Family Heating and Cooling will send Mauricio pictures of the unit, including the serial number and voltage readings, after the call. Spencer will order a replacement control board using the part number provided, likely through a local supplier such as Portland Group or FW Webb. Mauricio will create a warranty ticket for the old control board once Spencer returns it and will provide instructions for the necessary programming and configuration of the new board. |  | EODA18H2436BAA | na | na | 1402220I0CW13246L000126 | MCB | EAC230904173
24159 | 2026-02-18 | 2026 | 2 | 2026-02 | E-code | TRUE | medium | improper flame sensor position | mechanical | TRUE | FALSE | Control Board | E0 | na | NA |  |  |  | 2026-02-10 |  | unknown | site visit for E 8 error code on furnace | site visit for error code on furnace .Tested gas pressure and adjusted to factory settings . tested flame sensor readings . found on first stage reading at below 1 and second stage at 1.6 . moved flame sensor closer to front of burner and reading change to 1.6 on first and second stage . tested system for two hours and reading was the same . | E8 | na | na | MGH96M100C5A | na |  | na
24193 | 2026-02-20 | 2026 | 2 | 2026-02 | MCB | TRUE | high | faulty condenser board | control_board | FALSE | TRUE | unknown |  | EODA18H4860 | EODA18H | 1.5 |  |  | 2026-02-19 |  | unknown | bad board and EMI filter at condenser per Joshua | bad board and EMI filter at condenser |  | EODA18H4860 | na | na | 16015KW417ZK60300138 |  | EAC230904171/EAC230904159
24201 | 2026-02-20 | 2026 | 2 | 2026-02 | MCB | TRUE | high | faulty air handler board | control_board | FALSE | TRUE | unknown |  | na | NA |  |  | 2022-09-28 | 2026-02-20 | 1241 | >2y | bad board at air handler | Lorenzo (Technician, Whiteley Plumbing, Heating, and Cooling) initiated a call regarding an intermittent issue with an indoor air handler that causes the internal breaker to trip. The heater elements are not receiving power, although low voltage is detected on the circuit board. Mauricio Cordeiro (Support Representative, Geekho) asked clarifying questions to understand the wiring and components involved in the air handler's operation. Lorenzo explained that the circuit board shows no signs of damage but isn't powering the heating elements, leading to the suspicion of a faulty board. Mauricio guided Lorenzo through testing the heater element and checking the circuit board connections to troubleshoot the issue. They discussed the model number of the unit, which is EAHATN48, and its warranty status. Mauricio informed Lorenzo that the circuit board is under warranty, but the heating element is not. After some testing, they confirmed that the heating element is functioning correctly, with a current reading of 19 amps on one of the coils. Mauricio will provide a part number for the replacement board and create a ticket for warranty purposes. The conversation concluded with Mauricio offering further assistance and providing the part number needed for the repair. |  | na | EAHATN48 | na | na | AHU Motherboard | EAC1099000009(03/09/26), EHK10B(03/05/26) 36K-FLF001
24203 | 2026-02-21 | 2026 | 2 | 2026-02 | MCB | TRUE | high | defective MCB board | control_board | FALSE | TRUE | Other | . | . | . | [5 empty] | unknown | Bad MCB | Bad MCB Wholesaler did the tech support (We need to ship the part) |  | . | EAHATN-48 | . | . | MCB | 230904222
24258 | 2026-02-25 | 2026 | 2 | 2026-02 | Leakage | TRUE | high | evaporator coil leak | refrigerant | FALSE | TRUE | Other | na | EODA18H-4860 | EODA18H | 1.5 |  | 2021-06-26 | 2026-02-23 | 1703 | >2y | coil leak at indoor air handler | The wireless technician arrived at a job site last week to address a heat pump issue where the heat was not working, and added one pound of refrigerant with dye to the system. During a follow-up leak search today, the technician found dye inside the indoor coil, indicating a leak in that area. The technician took four pictures of the indoor coil showing the dye and is currently on site, ready to send the photos to Mauricio Cordeiro for review. Tasks The technician will send the four pictures of the indoor coil with dye to Mauricio Cordeiro for further analysis. |  | EODA18H-4860 | EAHATN-36 | na | 1C930WKB00ZKB1900160 | Evaporator assembly | EAC1099000008
24262 | 2026-02-25 | 2026 | 2 | 2026-02 | Leakage | TRUE | high | evaporator coil leak | refrigerant | FALSE | TRUE | Other | na | EODA18H-2436BAA | EODA18H | 1.5 |  | 2025-03-12 | 2026-02-23 | 348 | 31-365d | coil leak at air handler | Kenny (Technician, Air Incorporated) initiated the call regarding a leak search on an E-Core condenser and air handler, noting an oil buildup. Mauricio Cordeiro (Technical Support Representative, Air Incorporated) inquired about the pressure testing method and current pressure readings. Kenny reported a pressure of 523 but no visible bubbles, leading to confusion about the leak's source. The two discussed previous issues with older units, establishing that the current coils typically do not have leak problems. Kenny confirmed that the unit was recently installed, and they discussed the unit's location and performance history. Mauricio asked for the last six digits of the serial number to access the unit's details, streamlining the information retrieval process. A deeper investigation into the oil location and possible causes of the leak was discussed, focusing on the TXV's condition. Kenny shared pictures of the oil buildup, and they explored possible leaking points, including the TXV. Mauricio suggested that the issue might be with the TXV rather than the coil, noting that new coils should not leak under normal conditions. The conversation concluded with Mauricio creating a ticket for a replacement part, ensuring Kenny would receive credit for the old coil. |  | EODA18H-2436BAA | EAHATN-36BAA | na | 167TWWQ500ZQ50800030 |  | EAC1099000008
24284 | 2026-02-26 | 2026 | 2 | 2026-02 | MCB | TRUE | high | main control board failure | control_board | FALSE | TRUE | Other | na | EODA18H4860 | EODA18H | 1.5 |  |  | 2026-02-25 |  | unknown | bad board per Chris Morley | Tech Support - SILVA ROBERT identified a problem with a computer board and confirmed it should be under warranty, needing a claim number to proceed. He checked stock at FW Webb in Hyannis, which has one unit available, and was instructed to call to obtain a claim number before they will bring the unit in. The unit does not have a gateway, and SILVA ROBERT plans to send a picture of the model for further identification. Mauricio Cordeiro asked if SILVA ROBERT took pictures of the board and requested the model number for verification. Tasks Tech Support - SILVA ROBERT will send a picture of the computer board's model to Mauricio Cordeiro. Tech Support - SILVA ROBERT will call to obtain a claim number before FW Webb in Hyannis brings the replacement unit. |  | EODA18H4860 | na | na | 1W967600ZM71401783 | MCB | EAC230904171
24312 | 2026-02-27 | 2026 | 2 | 2026-02 | MCB | TRUE | high | surge induced board failure | control_board | FALSE | TRUE | Other | na | EODA18H4860 | EODA18H | 1.5 |  |  | 2026-02-26 |  | unknown | bad board at condenser | Tech Support Tyler reported that the outdoor fan of a heat pump system was not operating, and Mauricio confirmed the system's online status via the serial number, noting alerts indicating a charge limit issue. Mauricio identified the outdoor unit as model Alpha 18, Henry 48600, serial number starting with 1 Alpha 681 Walter Mary 6000, and confirmed no warranty report was filled out, indicating no existing warranty documentation. The system lacked a surge protector, which Mauricio emphasized is critical in Massachusetts to prevent board failures, as unprotected units often have their boards damaged, costing approximately $1,800 per repair. Mauricio instructed Tyler to check voltage at the EMI filter and main board, and to verify the compressor wiring and grounding, concluding that the board was likely bad due to the absence of a surge protector and the system's age. Mauricio provided the part number 230-904171 for the replacement board, explained the need to adapt the new board to the unit's configuration, and instructed Tyler to follow specific programming steps after installation. Mauricio advised Tyler to install a surge protector on the disconnect to protect the new board, and to send him pictures of the model and serial numbers for warranty processing. Mauricio committed to sending a warranty ticket and instructed Tyler to return the old board for credit, emphasizing the importance of installing surge protectors to avoid costly future repairs and warranty voidance. Tasks Tech Support Tyler will send Mauricio a picture of the model and serial numbers of the indoor and outdoor units via text message. Tech Support Tyler will install the new control board following Mauricio's instructions and send Mauricio a picture of the installed surge protector on the disconnect. Tech Support Tyler will return the old control board to the supply house for warranty credit after installation. Mauricio will send a warranty ticket to Tech Support Tyler once he receives the necessary pictures and information. |  | EODA18H4860 | na | na | 1A681WM600ZM60500481 | None;MCB | EAC230904171
24314 | 2026-02-27 | 2026 | 2 | 2026-02 | Leakage | TRUE | high | indoor coil leak | refrigerant | FALSE | TRUE | Compressor | low ref. Leaking coil. oil in pan. | EAHATN-36 | EAHATN | 3 |  | 2024-01-08 | 2026-02-26 | 780 | >2y | Leaking Coil - Please credit The Portland Group Providence for EAC1099000008 | Contracto called to home for lack of heat. System was low on ref. Recharged. Found oil on IDU pan. Photos attached Please credit The Portland Group Providence for EAC1099000008 |  |  | EAHATN-36 |  |  | Evaporator assembly | EAC1099000008
24315 | 2026-02-27 | 2026 | 2 | 2026-02 | Sensor | TRUE | medium | liquid line sensor failure | electrical | FALSE | TRUE | Sensor | F3 | EODA18H4860 | EODA18H | 1.5 |  |  |  |  | unknown | bad temp sensor at condenser | Tech Support from Eagle HVAC reported an F3 error code on the outdoor unit, indicating a faulty liquid line sensor. The unit model number is E, eau de 18, with serial number L 753 whiskey 50 zebra 51, and no IoT Gateway present. The technician confirmed the sensor connected to the liquid line was reading as an open line, indicating it is faulty. Mauricio advised unplugging the sensor, testing its resistance between 0.5K and 350K ohms, and replacing it if readings are outside this range. Mauricio identified the sensor as a CN4 black connector on the control board, with the sensor wires connected to the liquid side and high side sensors. Mauricio will send a part number for the replacement sensor to the technician's phone number in Framingham and create a support ticket with the unit's model and serial numbers. The technician's name is Jelson G., from Eagle HVAC, and they are of Brazilian origin. Tasks Mauricio will send the part number for the liquid line sensor to Jelson G. via text message. Mauricio will create a support ticket using the unit's model and serial number information. |  | EODA18H4860 | na | na | 1L753WL500ZL51800012 | Choose the part that is needed. | EAC2309100023
24316 | 2026-02-27 | 2026 | 2 | 2026-02 | MCB | TRUE | high | outdoor unit control board failure | control_board | FALSE | TRUE | Protection | PA | EODA18H2436 | EODA18H | 1.5 |  |  | 2026-02-26 |  | unknown | bad board at condenser | Philip swapped motors between units and confirmed that the motor itself was functional, indicating the control board was likely the issue. Mauricio advised that the control board costs approximately $1800 and recommended installing a surge protector to prevent future damage due to power issues. Philip is in Massachusetts and will send Mauricio a picture of the model and serial numbers of the unit to obtain the correct part number. Mauricio will generate a warranty ticket and instruct Philip to return the faulty board when replacing it. They discussed the new universal control board that fits multiple units, which requires a one-time setup using a dip switch, with instructions included in the packaging. Mauricio recommended ordering parts from Web or Portland Group, noting that Portland Group has a broader parts inventory. Philip agreed to order the parts and will send Mauricio the company name and order details via message. Mauricio emphasized the importance of installing a surge protector on the units to prevent electrical damage, especially in areas with voltage fluctuations. They agreed that Mauricio is available for technical support via cell phone if Philip encounters issues during installation or setup. Tasks Philip will send Mauricio a picture of the model and serial number of the unit to confirm the correct part number. Philip will order the control board from either Web or Portland Group and send Mauricio the company name and order confirmation. Mauricio will generate a warranty ticket for the faulty control board and inform Philip of the ticket number. Philip will inform the customer about the necessity of installing a surge protector on the unit to prevent future electrical issues. |  | EODA18H2436 | na | na | 1A521WM400ZM42001091 | MCB | EAC230904173
24325 | 2026-02-27 | 2026 | 2 | 2026-02 | MCB | TRUE | high | blank control board display | control_board | FALSE | TRUE | Other | 12/2025 | EODA18H 2436 | EODA18H | 1.5 |  |  | 2026-02-26 |  | unknown | blank board at condenser with surge protector | blank board at condenser . has 246 volts going to the board and a blank display |  | EODA18H 2436 | na | na | 1A521WM700ZM71401915 | MCB | EAC230904173
24335 | 2026-02-27 | 2026 | 2 | 2026-02 | MCB | TRUE | high | dead control board display | control_board | FALSE | TRUE | Other | No display | EODA19H-2436AAA | EODA19H | 2 |  |  | 2012-10-25 |  | unknown | Please credit TPG Raynham for a EAC230904165. Ordered on PO P1700440 | Contractor called to home for no heat. determined board was bad. Had no display. Contractor replaced the board on 1/6/2026 and it now up and running. Please credit TPG Raynham for a EAC230904165. Ordered on PO P1700440 |  | EODA19H-2436AAA |  |  | 0EWH003129Z243150065 | MCB | EAC230904165
24343 | 2026-02-28 | 2026 | 2 | 2026-02 | Sensor | TRUE | medium | faulty condenser sensor | electrical | FALSE | TRUE | Control Board | E7/P7 | EODA19H2436AAA | EODA19H | 2 |  |  | 2026-02-26 |  | unknown | bad td sensor at condenser | bad sensor at condenser per Joshua . |  | EODA19H2436AAA | na | na | OEWH003523Z24A100049 | Other | E.AC.2309100007
24375 | 2026-03-02 | 2026 | 3 | 2026-03 | MCB | TRUE | high | stuck reversing valve relay | control_board | FALSE | TRUE | Other | na | EODA18H-2436 | EODA18H | 1.5 |  | 2019-12-16 |  |  | unknown | Faulty Board | Faulty Board. system stuck in heating even removed all control wires. |  | EODA18H-2436 | GN1836-P1 | . | 12670WIC550J21200001 | MCB | EAC230904173
24376 | 2026-03-03 | 2026 | 3 | 2026-03 | MCB | TRUE | medium | incorrect replacement part | control_board | TRUE | TRUE | Other | na | EODA18H-4860BAA | EODA18H | 1.5 |  | 2025-08-05 | 2026-03-02 | 209 | 31-365d | bad board at air handler | Olivia from Broncos Heating contacted Mauricio from ecore about a wrong circuit board received for an indoor unit, which was installed but did not fit properly. The incorrect board was sent after a technician identified it as the wrong part; the correct board has wires attached and matches the original green board. Olivia provided Mauricio with images of the installed board, the received board, and the model and serial numbers, to assist in locating the correct replacement. Mauricio confirmed he has some of the correct boards in Maine and will create a ticket number and send Olivia the part number and ticket details for shipment. The call ended with Mauricio planning to send the correct board and Olivia looking forward to receiving the text messages with the tracking information. Tasks Mauricio from ecore will locate the correct circuit board in Maine and create a ticket for its shipment. Mauricio will send Olivia the part number and ticket details via text message. Olivia from Broncos Heating will await the text messages with the tracking information for the correct circuit board. |  | EODA18H-4860BAA | EAHATN-60 | na | 166I6WQ500ZQ52100189 | Other | 36K-FLF001
24379 | 2026-03-03 | 2026 | 3 | 2026-03 | MCB | TRUE | high | burnt outdoor circuit board | electrical | FALSE | TRUE | Other | na | ESCA16H-36 | ESCA16H | 3 |  |  | 2026-03-02 |  | unknown | burned board at condenser with surge protector | The wireless tech support representative reported that the outdoor unit's circuit board appears burnt, with Mauricio Cordeiro confirming the damage is on the board receiving power from the disconnect and instructing to send a photo for evaluation. Mauricio Cordeiro checked voltage on wires, indicating that if no voltage is present outside, there may be an issue with the breaker or wiring, and suggested replacing the breaker if necessary. The representative confirmed no other boards appeared burnt and mentioned having an electrician on site, though they observed no voltage outside the unit, which is inconsistent with Mauricio's expectations. Mauricio Cordeiro planned to send the part number of the damaged board via text message and create a warranty ticket, advising the electrician to verify power supply after replacement. The representative agreed to send the company and personal information for the warranty process. Tasks Wireless tech support representative will send Mauricio Cordeiro a picture of the burnt circuit board via text message. Mauricio Cordeiro will send the part number of the damaged board to the representative via text message. Mauricio Cordeiro will create a warranty ticket for the damaged board once the representative provides their company and personal information. |  | ESCA16H-36 | na | na | 3EWH001244Z2420110002 |  | EAC17122000062589
24393 | 2026-03-03 | 2026 | 3 | 2026-03 | MCB | TRUE | high | power surge damage | electrical | TRUE | TRUE | Other | Blank display | EODA18H-2436 | EODA18H | 1.5 |  |  |  |  | unknown | Blanks display, no surge protector | Blanks display, no surge protector. Told contractor that surge protector is REQUIRED on every Ecoer systems. They will need to install one and send us a picture to get the board reimbursed. |  | EODA18H-2436 | . | . | 1A521WM700ZM70301699 | MCB | EAC230904173
24403 | 2026-03-04 | 2026 | 3 | 2026-03 | MCB | TRUE | medium | incorrect field wiring configuration | electrical | TRUE | TRUE | Other | na | EODA18H2436 | EODA18H | 1.5 |  |  | 2026-03-03 |  | unknown | Bad board at condenser | Alex Valentine (Technician, Boston Standard) called regarding an EODA18 unit displaying zero on the LED board while receiving a Y signal. Mauricio Cordeiro (Technical Support Representative) guided Alex through troubleshooting steps, including checking connections and voltage. The conversation revealed that the unit had an overvoltage issue, with 25 volts detected at O, indicating it was not correctly configured for heating. Mauricio confirmed that the proper connection for the system should only have voltage on Y for heating, and instructed Alex to bypass the thermostat for testing. They discussed the need for a new board and Mauricio provided a part number (EAC2309) for ordering. Mauricio emphasized the importance of adding a surge protector to the unit and confirmed the voltage was acceptable at 244 volts total. The call concluded with Mauricio requesting Alex's name and company information to create a ticket for warranty purposes. In the conversation, Alex Valentine (Technician, Boston Standard) reached out to Mauricio Cordeiro (Technical Support Representative) for assistance with an EODA18 unit that was showing a zero on the LED board while receiving a Y signal.Mauricio guided Alex through various troubleshooting steps, discovering an overvoltage issue that indicated an incorrect configuration. They established that the unit required a new board and discussed the necessity of a surge protector.The call ended with Mauricio asking for Alex's details to proceed with a warranty ticket for the replacement part. |  | EODA18H2436 | na | na | 1W123M300ZM32301087 | MCB | EAC230904173
24430 | 2026-03-05 | 2026 | 3 | 2026-03 | Leakage | TRUE | high | evaporator coil leak | refrigerant | FALSE | TRUE | Other | na | EODA18H-4860 | EODA18H | 1.5 |  | 2023-06-30 |  |  | unknown | Coil Leak | Coil Leak |  | EODA18H-4860 | EAHATN-36 | . | 1A681WM600ZM60500543 | Evaporator assembly | EAC1099000008
24431 | 2026-03-05 | 2026 | 3 | 2026-03 | MCB | TRUE | high | faulty outdoor control board | control_board | FALSE | TRUE | Other | na | EODA18H-2436 | EODA18H | 1.5 |  | 2022-05-20 | 2026-03-04 | 1384 | >2y | blank board at condenser with 248 volts and surge protector | The wireless caller reported that the outdoor control unit was faulty, with the display blank and inconsistent operation, despite 240 volts input and 24 volts output. The caller checked voltage on the Y and C terminals, confirming 24 volts, but noted only a call for cooling, not heating, which was confirmed by Mauricio. Mauricio identified that the thermostat and zone board configurations indicated a heat pump system with a 2-zone setup, and suggested that the zone board might be malfunctioning, causing the unit to only call for cooling. The caller was advised to disconnect the outdoor unit and test if the system runs on heat, which would indicate wiring or control board issues, and Mauricio recommended checking for wiring shorts or touches outside. The caller was instructed to verify the thermostat wiring, especially the red and yellow wires, and to perform a jumper test to confirm if the outside unit operates correctly when bypassing the control board. Mauricio offered to be available for follow-up via call or text after the caller performs these tests to further diagnose the problem. Tasks The wireless caller will check the thermostat wiring and perform a jumper test on the red and yellow wires outside, then contact Mauricio with the results. The wireless caller will verify the voltage at the outdoor unit after disconnecting it from the control board to see if the system runs on heat. |  | EODA18H-2436 | EAHATN-36 | na | 1O372WL800ZL80100006 | MCB | EAC230904173
24433 | 2026-03-05 | 2026 | 3 | 2026-03 | MCB | TRUE | high | main control board failure | control_board | FALSE | TRUE | Other | na | EODA18H-4860 | EODA18H | 1.5 |  | 2023-02-03 | 2026-03-04 | 1125 | >2y | blank board at condenser with 233 volts with surge protector | na |  | EODA18H-4860 | EAHATN-60 | na | 1W967WM400ZM40100328 | MCB | EAC230904171
24437 | 2026-03-05 | 2026 | 3 | 2026-03 | MCB | TRUE | high | burnt PCB and EMI | control_board | FALSE | TRUE | Other | na | EODA18H-4860 | EODA18H | 1.5 |  |  |  |  | unknown | Burnt board and EMI needs to be replaced. | Burnt board and EMI needs to be replaced. |  | EODA18H-4860 | . | . | 10608WL800ZL80700096 | EMi Filter;MCB | 231236289 (3/13/26), EAC231235532 (03/13/26), EAC230904171, 230904159, EAC230904303, EAC230904304
24438 | 2026-03-05 | 2026 | 3 | 2026-03 | Motor | TRUE | high | faulty inducer motor | mechanical | FALSE | TRUE | Refrigerant Circuit | C1, CF | . | . |  |  | 2023-10-01 |  |  | unknown | faulty inducer motor | faulty inducer motor |  | . | . | MGH96M060B3A | . | Other | 17400801002944
24457 | 2026-03-06 | 2026 | 3 | 2026-03 | Leakage | TRUE | high | evaporator coil leak | refrigerant | FALSE | TRUE | Other | na | . | . | [5 empty] | unknown | COIL LEAK | COIL LEAK. PREVIOUS CONTRACTOR DOES NOT WANT TO DO THE WORK. |  | . | EAHATN-48 | . | . | Evaporator Only | EAC1099000009
24467 | 2026-03-06 | 2026 | 3 | 2026-03 | MCB | TRUE | high | burned condenser board | control_board | FALSE | TRUE | Other | na | EODA18H4860 | EODA18H | 1.5 |  |  | 2026-03-05 |  | unknown | burned board at condenser | The caller attempted to reach Mauricio multiple times, but there was confusion about the correct phone number, leading to missed calls and miscommunication. They discussed ongoing HVAC issues at the caller's brother's property, including indoor unit shutdowns at 78°F, outdoor unit running continuously, high pressure codes, and potential board or thermostat problems. Mauricio advised checking for voltage outside between the Y and common terminals to diagnose whether the issue is inside or outside the unit, and suggested inspecting the thermostat and wiring. The caller reported previous repairs, including indoor fan motor replacement, and confirmed the outdoor unit's fuse was blown, requiring a new control board. They discussed upcoming service visits to Maine, including specific store locations and dates in April, and the importance of bringing surge protectors and verifying the condition of compressors. Mauricio agreed to create service tickets for the units needing repair and to send parts and warranty information, emphasizing the need for proper documentation and pictures during future inspections. |  | EODA18H4860 | na | na | 1W967WM600ZM62000438 | MCB | EAC230904171
24475 | 2026-03-06 | 2026 | 3 | 2026-03 | MCB | TRUE | high | grounded compressor and board | mechanical | FALSE | TRUE | Control Board | E0 | EODA18H-2436 | EODA18H | 1.5 |  |  |  |  | unknown | Grounded compressor, faulty board. | Grounded compressor faulty board. Tech needs to install a surge protector to keep the warranty. |  | EODA18H-2436 | . | . | 1W123WM200ZM20500637 | MCB;Compressor | EAC230904173, 231235530
24476 | 2026-03-07 | 2026 | 3 | 2026-03 | MCB | TRUE | high | control board failure | control_board | FALSE | TRUE | Other | 0 | EODA18H-4860. | EODA18H | 1.5 |  | 2025-08-28 | 2026-03-04 | 188 | 31-365d | Control board failure diagnosed - 3652 | The customer reported that the rear unit was not operating properly. After inspection, the unit displayed error code E0 (low voltage / under-voltage condition). The voltage at the unit was measured at 248V, which is within the normal operating range. The following electrical tests were performed on the compressor: Winding continuity test — OK Inspection for loose or defective electrical connections — none found Ground short test — OK Final diagnosis: control board failure. After replacing the board with a spare unit from stock, the system returned to normal operation. We kindly request a replacement board to replenish our stock as soon as possible. |  | EODA18H-4860. | 0 | 0 | 1O608WL900ZL92600053 |  | Control Board
24483 | 2026-03-07 | 2026 | 3 | 2026-03 | Leakage | TRUE | high | condenser coil leak | refrigerant | FALSE | TRUE | Other | na | EODA18H-2436 | EODA18H | 1.5 |  | 2020-06-24 |  |  | unknown | condenser coil leak | condenser coil leak. tech will send pics. |  | EODA18H-2436 | EAHATN-36 | . | 11649WJ1560J42300036 | Other | EODA18H-2436
24512 | 2026-03-09 | 2026 | 3 | 2026-03 | MCB | TRUE | high | main control board failure | control_board | FALSE | TRUE | Other | N00 | EODA18H-4860 | EODA18H | 1.5 |  |  |  |  | unknown | Motherboard Stuck on N00 setting | Motherboard Stuck on N00 setting |  | EODA18H-4860 | . | . | 12673WK251ZK51900034 | MCB | EAC230904171
24514 | 2026-03-09 | 2026 | 3 | 2026-03 | MCB | TRUE | high | shorted compressor motor | mechanical | FALSE | TRUE | Other | blank screen | EODA18H-4860 | EODA18H | 1.5 |  | 2022-07-14 |  |  | unknown | Blanks display on board. Breaker tripped. | Blanks display on the board. The breaker tripped. compressor ohms 0.6 0.7 0.6 |  | EODA18H-4860 | EAHATN-48 | . | 1W967WM300ZM32200143 | MCB | EAC230904171
24516 | 2026-03-09 | 2026 | 3 | 2026-03 | Charge | TRUE | medium | low refrigerant charge | refrigerant | FALSE | FALSE | Protection | P1 | EODA18H-2436 | EODA18H | 1.5 |  |  |  |  | unknown | Charge issue possibly | Charge issue possibly . |  | EODA18H-2436 | GNC3036BPT | . | 1D003WKB00ZKB2000140 |  | na
24521 | 2026-03-10 | 2026 | 3 | 2026-03 | MCB | TRUE | medium | loose control board connection | control_board | TRUE | FALSE | Other | na | na | NA |  |  |  | 2026-03-09 |  | unknown | bad board at air handler | ReviSe Energy's tech support contacted Mauricio regarding a customer's heating system malfunction where the heat stopped working and the condenser shut off within five minutes, with the discharge and liquid lines at the same temperature. The technician observed the fan was off, checked wiring and voltage (24V on G), and tested the reversing valve, confirming the system was in cooling mode. When the technician manually bridged R and G wires, the fan started, indicating a possible loose connection on the control board. The technician pressed the control board into its bracket with power off, which restored fan operation, suggesting a loose connection on the board itself. Mauricio advised that the loose connection is likely on the control board and warned that the issue might recur, leading to future customer calls. They discussed the part number for the replacement control board, with Mauricio confirming the part number as Echo Alpha Charlie 230904222, and that they have sufficient stock in Dallas. Mauricio recommended the technician order the replacement from Portland Group, ensuring all wiring connections are secure before installation. A support ticket will be created for the replacement under warranty, and Mauricio requested a picture of the system's serial and model numbers to generate the ticket. Tasks Mauricio will send the technician the support ticket number after creating it. The technician will send a picture of the system's serial and model numbers to Mauricio. The technician will order the replacement control board (part number Echo Alpha Charlie 230904222) from Portland Group and ensure all wiring connections are secure during installation. |  | na | EAHATN -36 BAA | na | na | MCB | 230904148 (3/17/26), EAC230904222
24526 | 2026-03-10 | 2026 | 3 | 2026-03 | MCB | TRUE | high | power surge damage | control_board | FALSE | TRUE | Other | blank screen | EODA18H-2436 | EODA18H | 1.5 |  | 2022-05-31 |  |  | unknown | Burnt Board | Burnt Board. No surge protector. advised contractor to install a surge protector when he goes back. |  | EODA18H-2436 | GNC3036BPT | . | 1J339WL400ZL40100157 | MCB | EAC230904173
24537 | 2026-03-10 | 2026 | 3 | 2026-03 | MCB | TRUE | high | voltage fluctuation damage | control_board | FALSE | TRUE | Control Board | E0/C1/C7/C2/CB | EODA18H-2436 | EODA18H | 1.5 |  | 2023-10-09 | 2026-03-10 | 883 | >2y | bad board at condenser . | Sean from dual Plumbing Heating and Cooling reported a C1 error code on the HVAC system, which cycles repeatedly after startup. Mauricio identified the error as related to voltage fluctuations and recommended installing surge protectors and a transformer to stabilize incoming power, especially given the high and erratic voltage levels observed on the site. The system's control board was determined to be damaged due to voltage issues, and Mauricio provided the part number (EAC23Z) for a replacement board, advising the technician to install a surge protector to prevent future damage. The technician was instructed to shut off the unit, check the compressor wiring and resistance, and verify that the voltage at the compressor matches the input voltage, which was around 212V per leg. It was discussed that high and unstable voltage is common in the area, especially on the Cape, due to external factors like solar power feed-in, leading to equipment damage; installing a transformer and surge protection is recommended to mitigate these issues. Tasks Mauricio will send Sean the part number EAC23Z for the control board via text message. Sean will install a surge protector on the HVAC system to prevent future voltage-related damage. Sean will verify the compressor wiring resistance and ensure the voltage at the compressor matches the input voltage during the next service visit. Mauricio will create a service ticket for the replacement board and include a note about installing a surge protector, to be used for warranty and future reference. |  | EODA18H-2436 | EAHATN-24 | na | 1O372WL900ZL92500081 | MCB | 231235530 (04/09/26), EAC230904173
24538 | 2026-03-10 | 2026 | 3 | 2026-03 | Leakage | TRUE | high | evaporator coil leak | refrigerant | FALSE | TRUE | Other | na | EODA18H-4860 | EODA18H | 1.5 |  | 2023-04-13 | 2026-03-10 | 1062 | >2y | coil leak at air handler | Bailey Donald reported a refrigerant leak at 32 Brook Ridge Drive, Avon, Connecticut, with a coil leak confirmed via electronic leak detector showing 10 parts per million, but no visible leak was seen. Bailey confirmed the presence of a Gateway device on the system, with the last 6 serial number digits being 106455, which Mauricio planned to retrieve and use for system queries. The system is a 4-ton coil with a 4-ton air handler, and the refrigerant leak is associated with the coil. Mauricio discussed upcoming training sessions in Connecticut, Maine, and New Hampshire, including a planned event at the end of April or beginning of May, to showcase new units and provide technical training. They coordinated obtaining a part number for the leak repair, to be sent via text, and discussed the possibility of Bailey attending the training sessions. Mauricio mentioned plans to visit various supply stores in Connecticut, including FW Webb, Maya Supply, and Wind Supply, to conduct training and promote new units, with specific dates in late April and early May. They discussed Mauricio's schedule, including visits to Greenfield, Bridgewater, and Hartford, Connecticut, and the potential for Bailey to join upcoming training events. Tasks Mauricio Cordeiro will retrieve and send the Gateway serial number (last 6 digits: 106455) to Bailey Donald within 10 minutes. Mauricio Cordeiro will build and send a case number related to the leak repair and system query within approximately 6 minutes. Bailey Donald will confirm if their company has an account with FW Webb, Maya Supply, or Wind Supply to facilitate upcoming training sessions and parts procurement. Mauricio Cordeiro will finalize and send the part number for the leak repair to Bailey Donald after inputting the data into his system. |  | EODA18H-4860 | EAHATN-48 | na | 1A681WM600ZM60500563 | Evaporator assembly | EAC1099000009
24539 | 2026-03-10 | 2026 | 3 | 2026-03 | MCB | TRUE | high | control board failure | control_board | FALSE | TRUE | Other | Blank board display | EODA18H-2436 | EODA18H | 1.5 |  | 2022-10-01 |  |  | unknown | Blank display, Contractor will add a surge protector | Blank display, Contractor will add a surge protector |  | EODA18H-2436 | . | . | 1W123WM300ZM32300914 | MCB | EAC230904173
24548 | 2026-03-11 | 2026 | 3 | 2026-03 | Leakage | TRUE | high | indoor coil leak | refrigerant | FALSE | TRUE | Other | na | EODA18H-4860 | EODA18H | 1.5 |  | 2021-07-21 | 2026-02-10 | 1665 | >2y | coil leak at indoor unit | The call involved troubleshooting a heat pump system with Guadalupe Valle, discussing error codes, system status, refrigerant levels, and leak detection. Mauricio provided guidance on diagnostics, system reset procedures, and arranging for replacement parts, including shipping details. Recap Guadalupe Valle reported that the heat pump's compressor was not activating, with the system displaying an H0 code indicating it's a heat pump not calling for cooling or heating. The technician confirmed the system's serial number is 103952, and the system has been offline since Mauricio checked the status, with the display showing 80 and the fan running but no compressor activity. Mauricio explained that the H0 code indicates the system is not calling for heat or cool, and the technician's pressure readings of 55 PSI suggest low refrigerant levels, likely due to a leak in the coil. Guadalupe Valle identified a leak in the coil, observed oil in the pan, and confirmed the leak's location. They discussed the refrigerant charge status, with gauges showing no Freon in the system, and the system being locked out due to low pressure. Mauricio advised to check the low-pressure switch, verify the refrigerant charge, and perform a leak repair. He instructed Guadalupe Valle to send pictures of the leak and provided instructions for recharging the system, including monitoring pressure and superheat levels. The technician mentioned the system is in cooling mode with outside temperature at 79°F. Mauricio suggested ensuring the thermostat is set correctly and confirmed the system's refrigerant charge is insufficient, requiring a leak repair and recharge. Mauricio arranged to send a shipping form to Guadalupe Valle for a replacement coil, requesting company details and address. They also discussed the warranty registration and the need to contact the warranty provider for further assistance. Tasks Mauricio will send a shipping form to Guadalupe Valle for the coil replacement, requesting company name, address, and email. Guadalupe Valle will send Mauricio photos of the coil leak and the refrigerant gauge readings. Guadalupe Valle will verify and ensure the thermostat is set to cooling mode and monitor the system after leak repair and recharge. Guadalupe Valle will contact the warranty provider to confirm the system's warranty registration and process for the coil replacement. |  | EODA18H-4860 | EAHATN-48 | na | 1J340WL400ZL40100123 | Evaporator assembly | EAC1099000009
24549 | 2026-03-11 | 2026 | 3 | 2026-03 | Leakage | TRUE | high | coil leak | refrigerant | FALSE | TRUE | Other | na | . | . | [5 empty] | unknown | COIL LEAK | COIL LEAK |  | . | EAHATN-24 | . | . | Evaporator Only | EAC1099000008
24550 | 2026-03-11 | 2026 | 3 | 2026-03 | Leakage | TRUE | high | coil leak | refrigerant | FALSE | TRUE | Other | na | . | . | [5 empty] | unknown | COIL LEAK (2nd unit) | COIL LEAK |  | . | EAHATN-24 | . | . | Evaporator Only | EAC1099000008
24564 | 2026-03-12 | 2026 | 3 | 2026-03 | Leakage | TRUE | high | coil leak | refrigerant | FALSE | TRUE | Other | na | . | . | [5 empty] | unknown | Coil Leak | Coil Leak. |  | . | EAHATN-60 | . | . | Evaporator assembly | EAC1099000009
24566 | 2026-03-12 | 2026 | 3 | 2026-03 | MCB | TRUE | high | faulty fan motor | mechanical | FALSE | TRUE | Protection | PA | EODA18H-4860 | EODA18H | 1.5 |  | 2023-07-07 |  |  | unknown | PA error | Fulaty motor |  | EODA18H-4860 | GNC4860CPT | . | 1O608WL800ZL80700445 | Blower Motor | EAC2323100001
24586 | 2026-03-12 | 2026 | 3 | 2026-03 | Leakage | TRUE | high | evaporator coil leak | refrigerant | FALSE | TRUE | Compressor | leaking coil | EODA18H-2436 | EODA18H | 1.5 |  | 2023-12-13 | 2026-03-06 | 814 | >2y | please ship asap | oil in pan and leak found in evap |  | EODA18H-2436 | EAHATN-24 |  | 1A521WM400ZM42401408 | Evaporator Only | evap coil for 12-13-2023
24587 | 2026-03-12 | 2026 | 3 | 2026-03 | Leakage | TRUE | high | evaporator coil leak | refrigerant | FALSE | TRUE | Compressor | leaking coil | EODA18H-2436 | EODA18H | 1.5 |  | 2022-12-19 | 2026-03-06 | 1173 | >2y | please ship asap | leaking evap and oil in drain pan |  | EODA18H-2436 | EAHATN-24 |  | 1W123WM100ZM11600208 |  | evap coil for ECREAHATN-24
24597 | 2026-03-12 | 2026 | 3 | 2026-03 | MCB | TRUE | high | shorted control board | electrical | FALSE | TRUE | Other | na | EODA18H-4860BAA | EODA18H | 1.5 |  | 2024-10-03 | 2026-03-12 | 525 | 1-2y | blank board and grounded compressor with surge protector . | The call involved troubleshooting a malfunctioning wireless monitoring device that was sparking and emitting smoke, leading to the recommendation of replacing the control board and installing a surge protector. The technician, Joel, was advised to disconnect wires, check grounding, and send pictures of the system components for further assessment. Mauricio provided part numbers for replacement parts and instructed Joel on safety precautions and next steps for repair. Recap Joel from absolute mechanical reported a wireless monitoring device emitting smoke and sparking, with the device being offline and showing no display, indicating a failed control board. Mauricio confirmed the device's serial number (last 6 digits 170) and installation date (April 19, 2024), and identified the system as a 4860 with a 5-ton capacity at 47 Federal Hills Road, Hollis, New Hampshire. Joel was instructed to turn off the power, remove the cover, and disconnect the blue, white, and red wires from the EMI filter above the main board to inspect for damage or smoke, especially near the top section of the condenser and the EMI filter area. Joel observed smoke near the top section of the condenser and the EMI filter, which Mauricio identified as a potential source of the issue. Joel checked the wiring and grounding, confirming the compressor was grounded and that the wires appeared connected properly, with voltage readings of approximately 240V going into the main board. Mauricio advised Joel to locate and inspect the surge protector, which was in a non-standard location, and to send pictures of the disconnect and surge protector, including whether the surge protector's indicator light was on. Joel confirmed the surge protector had no light and that the disconnect switch was in place; Mauricio explained that a missing or non-functioning surge protector could contribute to system damage. Mauricio recommended replacing the control board, which was confirmed to be blank and unresponsive, and provided part numbers for the replacement components, instructing Joel to order them from FW Webb. Joel was advised to shut down the system, replace the control board, and ensure the wiring and surge protector were correctly installed before restarting the system. Mauricio emphasized the importance of following proper safety procedures, including verifying wiring, grounding, and surge protection, and instructed Joel to send pictures of the system components for confirmation. Tasks Joel from absolute mechanical will send Mauricio pictures of the disconnect switch and surge protector, including the indicator light, to confirm proper installation. Mauricio will text Joel the part numbers for the replacement control board and surge protector for ordering from FW Webb. Joel will locate and replace the control board once the new parts arrive, following Mauricio's instructions and verifying wiring and surge protection before restarting the system. |  | EODA18H-4860BAA | EAHATN-60BAA | na | 151AOWP600ZP61400100 | MCB;Compressor | EAC23090417/ EAC2312355321
24611 | 2026-03-13 | 2026 | 3 | 2026-03 | MCB | TRUE | high | burnt control board | control_board | FALSE | TRUE | Other | na | EODA18H 2436 | EODA18H | 1.5 |  |  | 2026-03-13 |  | unknown | blank board at condenser with surge protector installed | This was a follow-up call with Kevin from Sonos fuel company regarding a replaced control board. Mauricio emphasized the importance of on-site visits and documentation, including pictures of the system components, for warranty and system verification purposes. Recap Kevin from Sonos fuel company explained that they replaced a burnt control board during storm activity, with the new board functioning properly after installation. Mauricio informed Kevin that company policy requires on-site presence and photographic documentation of system components, including the control board and surge protector, for warranty validation and system testing. Kevin acknowledged the policy and agreed to send pictures of the system components, including the model and serial numbers, via email, as the physical parts had been collected. Mauricio provided his contact information and emphasized the need for technicians to call him before visiting the site for future system checks, and to send pictures of the system components, especially the surge protector. Kevin confirmed he would gather the necessary pictures and send them to Mauricio, and Mauricio created a ticket for warranty purposes. Tasks Kevin from Sonos fuel company will send Mauricio pictures of the system components, including the control board, surge protector, and serial/model numbers, via email. Kevin will ensure that future site visits include a call to Mauricio before technicians arrive, and will provide the requested documentation for warranty validation. |  | EODA18H 2436 | na | na | 1W123WM100ZM11600264 | MCB | EAC230904173
24614 | 2026-03-13 | 2026 | 3 | 2026-03 | Leakage | TRUE | high | evaporator coil leak | refrigerant | FALSE | TRUE | Other | na | EODA19H-4860AAA | EODA19H | 4 |  | 2025-08-11 | 2026-03-13 | 214 | 31-365d | Coil Leak | Coil Leak |  | EODA19H-4860AAA | EAHATN-60 | . | 0EWH004249Z245070025 | Evaporator assembly | EAC1099000009
24623 | 2026-03-14 | 2026 | 3 | 2026-03 | MCB | TRUE | high | indoor outdoor communication error | control_board | FALSE | TRUE | Control Board | E0 | EODA18H-4860 | EODA18H | 1.5 |  |  |  |  | unknown | E0 error. compressor not grounded. ohms reading good. | E0 error. compressor not grounded. ohms reading good. |  | EODA18H-4860 | . | . | 1A681WM400ZM40100137 | MCB | EAC230904171
24654 | 2026-03-17 | 2026 | 3 | 2026-03 | MCB | TRUE | high | water ingress damage | control_board | TRUE | TRUE | Other | N00 | EODA18H-2436B | EODA18H | 1.5 |  |  | 2026-03-16 |  | unknown | Water got into the board and burnt the board. NO WARRANTY | Water got into the board and burnt the board. NO WARRANTY |  | EODA18H-2436B | . | . | 14RR8WP500ZP51800007 | MCB | EAC230904173
24664 | 2026-03-17 | 2026 | 3 | 2026-03 | Leakage | TRUE | high | evaporator coil leak | refrigerant | FALSE | TRUE | Other | na | . | . |  |  |  | 2026-03-17 |  | unknown | Coil Leak | Coil Leak |  | . | EAHATN-60 | . | . | Evaporator Only | EAC1099000009
24668 | 2026-03-18 | 2026 | 3 | 2026-03 | Drain Pan | TRUE | medium | cracked drain pan | drain_water | TRUE | TRUE | Other | . | . | . |  |  |  | 2026-03-17 |  | unknown | Drainage Pan I Number 4 | drain pan cracked due to over-titening. We will honor this one due to the issues thaty have happend here |  | . | EAHATN-60 | . | . | Drain Pan 1 | 230701514
24679 | 2026-03-18 | 2026 | 3 | 2026-03 | MCB | TRUE | high | failed control board | control_board | FALSE | TRUE | Other | na | EODA18H4860 | EODA18H | 1.5 |  | 2019-11-22 | 2026-03-18 | 2308 | >2y | blank board at condenser | The technician from New Richmond PQ reported a non-functioning control board that shows no display and does not start the cooling or heating system, despite having 240 volts input. Mauricio confirmed the technician is a professional and requested pictures of the control board and model number for further assessment. The technician provided multiple images of the control board and model details via text message, which Mauricio reviewed to verify the part. Mauricio explained the need for the technician's company to be registered with government agencies (CRN) to ship parts directly to the company, but he can ship to the technician's personal address if unregistered. Mauricio decided to send a replacement control board to the technician's home address and instructed the technician to perform specific tests before installing the new part. Mauricio also advised installing a surge protector to prevent electrical issues from damaging the control board. Tasks Mauricio will send a replacement control board to the technician's home address. Mauricio will provide the technician with a picture of a surge protector to install with the new control board. The technician will perform tests on the new control board before installation and call Mauricio for guidance. The technician will send Mauricio a picture of the control board's serial number and model for shipping verification. Mauricio will send a tracking number once the replacement part is shipped. |  | EODA18H4860 | na | na | 11649Wj4280j50800110 | MCB | EAC230904171
24685 | 2026-03-19 | 2026 | 3 | 2026-03 | MCB | TRUE | high | pfc circuit failure | control_board | FALSE | TRUE | Other | na | EODA18H-4860 | EODA18H | 1.5 |  | 2023-03-13 | 2026-03-18 | 1101 | >2y | blank board at condenser with 239 volts | Hurley Daniel reported a unit with power but no display on the control board, model number eov, a118H, 4860, installed on March 13, 2023, at 15 Old Survey Drive, Acting, Massachusetts. The unit has a PFC error alert, no blinking light on the side box, and voltage measurements of approximately 238-239 volts at the Emi filter and main board, indicating proper power supply. Mauricio Cordeiro advised testing the compressor wiring for ground traces, which was confirmed negative, indicating no grounding issues. The technician was instructed to disconnect the wires and measure voltage across them, which showed consistent readings of 7 across all pairs, suggesting the control board may be faulty. Mauricio recommended replacing the control board, which will come with a sheet for configuration settings, and installing a surge protector at the disconnect to prevent future damage. A warranty ticket will be created for the control board replacement, and the technician was advised to read the instructions carefully during installation to ensure proper setup. Tasks Mauricio Cordeiro will generate a warranty ticket and send the part number for the control board to Hurley Daniel. Hurley Daniel will order the control board from FW Webb, Portland Group, or Economy, and install a surge protector at the disconnect. Hurley Daniel will send pictures of the control board and voltage measurements as requested by Mauricio. Hurley Daniel will replace the control board and follow the configuration instructions provided, ensuring proper setup. |  | EODA18H-4860 | na | na | 1A681WM600ZM60500648 | MCB | EAC230904171
24686 | 2026-03-19 | 2026 | 3 | 2026-03 | MCB | TRUE | high | burnt control board | control_board | FALSE | TRUE | Other | na | EODA18H-4860 | EODA18H | 1.5 |  |  | 2026-03-18 |  | unknown | blank board at condenser with 239 volts and surge protector installed | IRIZARRY JUAN reported that the circuit board with serial number 3W967WM3000 is burnt out and needs replacement, noting that the new boards sent are better than the original ones. The issue appears related to power supply problems, possibly involving incorrect current or lack of a surge protector, which may be causing the boards to burn out. Mauricio requested pictures of the search protector to assess whether it is present or needs replacement, and agreed to have someone send these images. They discussed part numbers for replacement components, specifically the C230 part number, and agreed to order from the economy supply house. Both parties exchanged contact information and confirmed they will follow up with case numbers and additional pictures as needed. Tasks IRIZARRY JUAN will send Mauricio pictures of the search protector once they are taken. Mauricio will send IRIZARRY JUAN the part number for the C230 component. IRIZARRY JUAN will have a team member visit the site to take pictures of the search protector. Mauricio will create a case and provide the case number to IRIZARRY JUAN after completing the ticket. |  | EODA18H-4860 | na | na | 3W967WM300ZM20532200026 |  | EAC230904171
24687 | 2026-03-19 | 2026 | 3 | 2026-03 | MCB | TRUE | high | faulty outdoor control board | control_board | FALSE | TRUE | Protection | PA | EODA18H-4860 | EODA18H | 1.5 |  | 2026-03-16 | 2026-03-18 | 2 | ≤30d (infant) | new install with bad board | Matt is installing a new HVAC unit (model 48 60s) that is experiencing a fan failure and error code PA R, with a blinking blue light indicating connection status. Matt has a Gateway device connected to the system, with the last 6 serial number digits 2301 810, and reports error codes C2 and C7. The outdoor fan motor does not run during startup, despite the compressor and reversing valve functioning, and the fan spins freely when tested manually. Mauricio suggests the control board is likely faulty, as the motor and wiring appear correct, and recommends replacing the board. Matt will check voltage at the CN8 terminal and send pictures of voltage and surge protector for Mauricio's review. A new control board (part number EAC30) will be ordered through Matt's supply house, with a warranty ticket to be created for replacement. Matt plans to swap the control board and test the system, and Mauricio advises on adjusting dip switches and fan speed settings to optimize operation. The call also covered general HVAC troubleshooting, power issues in Massachusetts, and the benefits of advanced system monitoring via gateways. Tasks Mauricio will generate and send a warranty ticket number for the control board replacement within 10 minutes. Matt will send Mauricio pictures of voltage readings and surge protector status after testing the system. Matt will order the replacement control board (part number EAC30) through his supply house and coordinate its installation. Matt will test the control board by powering it up and checking voltage at the CN8 terminal, then report back with findings. Matt will adjust dip switches and fan speed settings on the air handler as per Mauricio's guidance to reduce noise and improve performance. |  | EODA18H-4860 | na | na | 1402220PFIW13246F000070 |  | EAC230904171
24694 | 2026-03-20 | 2026 | 3 | 2026-03 | Leakage | TRUE | high | evaporator coil leak埋 | refrigerant | FALSE | TRUE | Other | na | EODA18H-4860BAA | EODA18H | 1.5 |  | 2025-09-16 | 2026-03-19 | 184 | 31-365d | coil leak at air handler | Christian with Beard Denice reports a leak in the indoor evaporator coil of an HVAC system installed less than one year ago, identified through an electronic detector that went off and documented with a video. Christian is providing details about the leak and has taken a video as evidence; Mauricio is reviewing additional information to determine next steps. |  | EODA18H-4860BAA | EAHATN-60 | na | 151AOWP700ZP70500210 | Evaporator assembly | EAC1099000009
24696 | 2026-03-20 | 2026 | 3 | 2026-03 | MCB | TRUE | medium | communication fault settings | communication | FALSE | FALSE | Control Board | E4/G4/C1/C2 | EODA18H-2436 | EODA18H | 1.5 |  | 2023-10-31 | 2026-03-19 | 870 | >2y | bad board at condenser | Nick Quattrucci reported faults on unit 300169, including alarms indicating communication faults (E4) over the weekend, with specific issues related to H2 and G4 C2 error codes. Mauricio Cordeiro explained that the E4 error relates to communication faults between the mainship and the unit, and that the H2 error indicates temperature issues due to external conditions, suggesting adjustments to defrost settings based on snow levels. Mauricio advised ensuring that temperature settings for the furnace and heat pump are synchronized and set to the same values, and recommended changing defrost type to 'light snow' or 'heavy snow' depending on snow accumulation, to improve defrost cycles during winter. He also recommended setting temperature thresholds for electric backup units to be significantly below the outdoor temperature, such as -22°F for the heat pump and 15°F for electric backup, to prevent resource cutoff and improve capacity. Nick indicated he has access to the unit's settings and plans to make the recommended adjustments, and Mauricio advised him to verify voltage and perform testing on-site due to the unusual error codes, planning to review the error code definitions during his visit. Tasks Nick Quattrucci will visit the unit located approximately 5 minutes away to perform on-site troubleshooting and verify voltage, then call Mauricio back with findings. Mauricio Cordeiro will review the specific error codes (E4 and G4 S) to determine their meanings and guide further troubleshooting after Mauricio's visit. |  | EODA18H-2436 | GNC3036BPT | n a | 1A521WM400ZM42401594 | MCB | EAC230904173
24715 | 2026-03-21 | 2026 | 3 | 2026-03 | MCB | TRUE | high | grounded compressor | electrical | FALSE | TRUE | Other | na | EODA18H-4860 | EODA18H | 1.5 |  | 2022-04-12 | 2026-03-20 | 1438 | >2y | Blank board at condenser with 247 volts and no surge protector | The technician from Holyoke MA reported arriving on site to find wires removed from the compressor, which was grounded, indicating possible tampering or prior repair attempts. Mauricio confirmed the compressor was installed in 2021, is currently offline, and under parts warranty until 2:30, with the serial number ending in 181788. The technician suspected the compressor was faulty, likely due to previous issues with voltage spikes causing damage, and was advised to install a surge protector to prevent future damage. Mauricio provided guidance on obtaining the correct parts, including a part number (likely 2436), and emphasized the importance of installing surge protection due to dirty power conditions common in Massachusetts. The technician was instructed to send a picture of the voltage at the disconnect and the surge protector, and Mauricio agreed to generate a warranty ticket for the compressor replacement, requiring the technician's name and company. Discussion included the importance of proper electrical practices, the need for licensed electricians to install disconnects, and the common issue of voltage spikes damaging HVAC components in the region. Tasks The technician from Holyoke MA will send Mauricio a picture of the voltage going into the unit and the surge protector after installation. Mauricio will generate a warranty ticket for the compressor replacement within 10 minutes and send the ticket number to the technician. The technician will send Mauricio their name and company name via text message for the warranty documentation. The technician will check their inventory for the part number Mauricio provides and confirm availability before proceeding with the replacement. |  | EODA18H-4860 | na | na | 1O608WL900ZL92600078 | MCB | EAC230904171
24716 | 2026-03-21 | 2026 | 3 | 2026-03 | Compressor | TRUE | high | blank control board | control_board | FALSE | TRUE | Other | blank screen | EODA18H-4860 | EODA18H | 1.5 |  |  | 2026-03-20 |  | unknown | Blank display, compressor is not grounded. Surger protector installed. | Blank display, compressor is not grounded. Surger protector installed. |  | EODA18H-4860 | . | . | 1W967WM600ZM61202080 | MCB | EAC230904171
24719 | 2026-03-21 | 2026 | 3 | 2026-03 | Motor | TRUE | medium | fan motor mechanical interference | mechanical | FALSE | TRUE | Other | 0 | 0 | 0 |  |  | 2025-10-08 | 2026-03-20 | 163 | 31-365d | Fan motor failure. CM6184 | Technician Report Structural reinforcement was applied to the main duct in order to minimize potential vibrations and noise. After the intervention, an inspection was performed to verify if any abnormal noise was still present in the duct system. During the evaluation, the unit’s fan operation was checked. It was observed that when the fan was shutting down, an abnormal noise occurred, similar to something hitting internally. This behavior may indicate possible mechanical interference, loose internal components, or irregular deceleration of the fan assembly. Due to this condition, technician AL was contacted for further evaluation. He requested detailed information regarding the unit and the fan in order to proceed with a deeper analysis and determine the appropriate corrective action. The need for motor replacement was identified. A ticket will be opened with ECOER. |  | 0 | EAHETN-36HA | 0 | 0 | None;Fan Motor | 0
24739 | 2026-03-23 | 2026 | 3 | 2026-03 | MCB | TRUE | high | voltage fluctuation board damage埋 | control_board | FALSE | TRUE | Control Board | E0/C3 | EoODA18h4860 | EOODA18H | 1.5 |  |  | 2026-03-23 |  | unknown | bad board at condenser with 238 volts | Alcindor Marie reported voltage readings of approximately 238V before and after a filter, indicating voltage stability within acceptable range, but Mauricio identified voltage fluctuations as a potential cause of control board issues. Mauricio recommended replacing the control board and installing a surge protector to prevent damage from voltage fluctuations, and asked Alcindor to send pictures of the voltage readings, model number, and serial number for warranty processing. Mauricio advised Alcindor to contact the web supplier to order the replacement control board, and instructed to read the accompanying paperwork upon installation. Mauricio will create a warranty ticket for Alcindor, requiring the return of the old control board with the warranty number for credit, and asked Alcindor to send a message with their name and company for documentation. The call included a discussion about the reliability of heat pumps in Massachusetts, with Mauricio sharing his personal positive experience and emphasizing the importance of proper voltage regulation. Tasks Alcindor Marie will send Mauricio a picture of the voltage going into the control board, along with the model and serial number, as soon as possible. Alcindor Marie will contact the web supplier or FWF porting group to order the replacement control board, ensuring to read the paperwork that comes with it. Alcindor Marie will install the new control board and a surge protector, then send Mauricio a picture of the installed board for record-keeping. Mauricio will send Alcindor a warranty ticket with the warranty number once the information is received. Alcindor Marie will bring the old control board back when replacing it to receive credit, using the warranty number for reference. |  | EoODA18h4860 | na | na | 1W967WM400ZM40100276 |  | ESAC230904171
24769 | 2026-03-24 | 2026 | 3 | 2026-03 | MCB | TRUE | high | overvoltage damage to PCB | control_board | FALSE | TRUE | Control Board | E0/C9 | EODA18H2436 | EODA18H | 1.5 |  |  | 2026-03-23 |  | unknown | bad board won condenser with 253v and surge protector | Mauricio Cordeiro (Technical Support Specialist, Geekho) initiated the call, ready to assist Jonathan from HomeWorks Energy regarding a system issue. Jonathan reported a leak search followed by an E0 error and a brief C9 error. Mauricio confirmed the compressor's condition was fine but highlighted that the incoming voltage was too high at 253 volts. They discussed that high voltage could damage the system's board, suggesting a transformer to reduce voltage. Jonathan confirmed he would check the board, and Mauricio advised to obtain a voltage reducer to prevent future damage. Mauricio expressed his accessibility, emphasizing that he is the local contact for support, and provided his cell number for direct communication. They concluded with a plan for Jonathan to send his details for a warranty ticket and discuss further steps. They agreed on the necessity of installing the voltage reducer. The conversation began with Mauricio Cordeiro (Technical Support Specialist, Geekho) assisting Jonathan from HomeWorks Energy regarding a system issue.Jonathan detailed his findings, including a leak search and error codes E0 and C9. Mauricio confirmed the compressor was functioning but warned that the incoming voltage was too high, risking damage to the system.They discussed the need for a transformer to manage voltage levels. Mauricio also reinforced his availability as a local support contact and instructed Jonathan to send his details for a warranty ticket.They wrapped up by agreeing on the urgency of installing a voltage reducer to prevent further issues. |  | EODA18H2436 | na | na | 1A521Wm400Zm42401512 |  | EAC230904173
24771 | 2026-03-24 | 2026 | 3 | 2026-03 | MCB | TRUE | high | dead on arrival PCB | control_board | TRUE | TRUE | Other | BLANK DISPLAY | EODA18H-2436 | EODA18H | 1.5 |  | 2026-03-17 | 2026-03-24 | 7 | ≤30d (infant) | BLANK DISPLAY | BLANK DISPLAY ON SCREEN, BRAND-NEW INSTALL. |  | EODA18H-2436 | . | . | 1A521WM700ZM71402018 | MCB | EAC230904165
24772 | 2026-03-24 | 2026 | 3 | 2026-03 | MCB | TRUE | medium | incorrect thermostat wiring | electrical | TRUE | FALSE | Control Board | E0/C6 | EODA18H4860 | EODA18H | 1.5 |  | 2021-04-09 | 2026-03-23 | 1809 | >2y | bad board at condenser | Ricky (Technician, High Efficiency) contacted Ecoer support regarding two units in Chatham experiencing issues: one displaying an H2 error and the other an E0 error. Mauricio Cordeiro (Support Agent, E-Court) identified that the H2 error on the first unit was due to the system running on secondary heat because the gateway was offline due to non-payment of monitoring fees. Mauricio guided Ricky through voltage checks to diagnose the wiring of the first unit, discovering the W wire was not properly connected to the furnace, preventing the heat pump from functioning correctly. Mauricio identified that the minimum temperature setting on the first unit was set to 40 degrees, preventing the condenser from running in the current cold weather; he then guided Ricky on how to adjust this setting for testing purposes. Regarding the second unit displaying an E0 error, Mauricio instructed Ricky to power it off for five minutes and then perform ohm readings to check for grounding issues with the compressor wires. After confirming the ohm readings were within acceptable parameters, Mauricio requested Ricky to send photos of the meter readings, model number, and serial number for documentation. Mauricio identified the E0 error as a common issue in Massachusetts due to voltage fluctuations and emphasized the importance of installing surge protectors to prevent board damage. Mauricio confirmed that the second unit had a bad board and provided Ricky with a part number for replacement and instructions to adapt the new board to the unit. Mauricio offered his direct cell phone number for further assistance and explained the warranty process for the board replacement, requesting Ricky's name and company name for creating a warranty ticket. Mauricio stressed the importance of installing surge protectors during the board replacement to prevent future issues, given the high cost of the boards. Ricky (Technician, High Efficiency) called Ecoer support to troubleshoot two malfunctioning units in Chatham.Mauricio Cordeiro (Support Agent, E-Court) determined that the first unit's H2 error was due to a disabled gateway and incorrect wiring, leading to the system running on secondary heat. Mauricio guided Ricky through several tests, including voltage checks and adjustments to the minimum temperature setting.The second unit displayed an E0 error, which Mauricio attributed to voltage fluctuations common in Massachusetts. He guided Ricky through ohm readings and ultimately diagnosed a bad board, providing a replacement part number and emphasizing the necessity of installing surge protectors.Mauricio offered his direct contact information for ongoing support and detailed the warranty claim procedure. The call concluded with Ricky expressing his appreciation for Mauricio's assistance. |  | EODA18H4860 | na | na | 10608WL900ZL92600165 | Other | 230904159
24773 | 2026-03-24 | 2026 | 3 | 2026-03 | Gas Furnace | TRUE | high | failed furnace igniter | mechanical | FALSE | TRUE | Other | na | EODA18H-4860BAA | EODA18H | 1.5 |  | 2024-04-16 |  |  | unknown | Per Vikey, need to ship igniter to Canada | Per Vikey, need to ship igniter to Canada |  | EODA18H-4860BAA | . | MGH96M100C5A | 14RR9WP500ZP52300027 | Other | 17427600000007
24775 | 2026-03-24 | 2026 | 3 | 2026-03 | MCB | TRUE | medium | incorrect thermostat wiring | electrical | TRUE | FALSE | Control Board | E0/C6 | EODA18H4860 | EODA18H | 1.5 |  | 2021-04-09 | 2026-03-23 | 1809 | >2y | bad board at condenser | Ricky (Technician, High Efficiency) contacted Ecoer support regarding two units in Chatham experiencing issues: one displaying an H2 error and the other an E0 error. Mauricio Cordeiro (Support Agent, E-Court) identified that the H2 error on the first unit was due to the system running on secondary heat because the gateway was offline due to non-payment of monitoring fees. Mauricio guided Ricky through voltage checks to diagnose the wiring of the first unit, discovering the W wire was not properly connected to the furnace, preventing the heat pump from functioning correctly. Mauricio identified that the minimum temperature setting on the first unit was set to 40 degrees, preventing the condenser from running in the current cold weather; he then guided Ricky on how to adjust this setting for testing purposes. Regarding the second unit displaying an E0 error, Mauricio instructed Ricky to power it off for five minutes and then perform ohm readings to check for grounding issues with the compressor wires. After confirming the ohm readings were within acceptable parameters, Mauricio requested Ricky to send photos of the meter readings, model number, and serial number for documentation. Mauricio identified the E0 error as a common issue in Massachusetts due to voltage fluctuations and emphasized the importance of installing surge protectors to prevent board damage. Mauricio confirmed that the second unit had a bad board and provided Ricky with a part number for replacement and instructions to adapt the new board to the unit. Mauricio offered his direct cell phone number for further assistance and explained the warranty process for the board replacement, requesting Ricky's name and company name for creating a warranty ticket. Mauricio stressed the importance of installing surge protectors during the board replacement to prevent future issues, given the high cost of the boards. Ricky (Technician, High Efficiency) called Ecoer support to troubleshoot two malfunctioning units in Chatham.Mauricio Cordeiro (Support Agent, E-Court) determined that the first unit's H2 error was due to a disabled gateway and incorrect wiring, leading to the system running on secondary heat. Mauricio guided Ricky through several tests, including voltage checks and adjustments to the minimum temperature setting.The second unit displayed an E0 error, which Mauricio attributed to voltage fluctuations common in Massachusetts. He guided Ricky through ohm readings and ultimately diagnosed a bad board, providing a replacement part number and emphasizing the necessity of installing surge protectors.Mauricio offered his direct contact information for ongoing support and detailed the warranty claim procedure. The call concluded with Ricky expressing his appreciation for Mauricio's assistance. |  | EODA18H4860 | na | na | 1C930WK300ZkB1900066 | MCB | 230904159, EAC 230904171
24780 | 2026-03-25 | 2026 | 3 | 2026-03 | MCB | TRUE | high | PCB hardware failure | control_board | FALSE | TRUE | Other | Blank board display | EODA18H-4860 | EODA18H | 1.5 |  |  | 2026-03-24 |  | unknown | Blank display | Blank display |  | EODA18H-4860 | . | . | 1W967WM300ZM32200026 | MCB | EAC230904171
24800 | 2026-03-26 | 2026 | 3 | 2026-03 | MCB | TRUE | high | main control board failure | control_board | FALSE | TRUE | Other | na | EODA18H-4860 | EODA18H | 1.5 |  | 2023-05-24 | 2026-03-25 | 1036 | >2y | blank board at condenser with 245 v and surge protector | Alex from Shanks Heating and Cooling reported that the Gateway system had no display and no power indicator, despite voltage being present at the PCB, indicating a potential hardware issue. Alex confirmed the system was receiving approximately 248 volts, and checked voltage both before and after the EMI filter, with voltage present at the board's L1 and L2 terminals. Mauricio identified that the Gateway had no power lights blinking, suggesting a power issue, and confirmed the fuse was intact with continuity tested successfully. Alex had previously opened the compressor and measured 0.5 to 0.6 ohms across all three legs, and checked wiring continuity, indicating wiring was likely not the issue. Mauricio advised Alex to contact Wind Supply in Kearney to order a replacement board with part number EAC 1030, providing a warranty ticket number for the replacement. Mauricio instructed Alex to send pictures of the voltage meter and the search protector, and to read the instructions on the new board for proper setup after replacement. Alex agreed to send the requested pictures and to follow up with Wind Supply for the replacement part, and Mauricio offered ongoing support via phone or text. Tasks Mauricio will generate and send a warranty ticket number to Alex after inputting the call details. Alex will contact Wind Supply in Kearney to order the replacement board using part number EAC 1030. Alex will send Mauricio pictures of the voltage meter showing voltage input and the search protector as requested. Mauricio will review the pictures and provide further instructions if needed after receiving the images. |  | EODA18H-4860 | na | na | 1W967WM600ZM60100809 | MCB | EAC230904171
24815 | 2026-03-26 | 2026 | 3 | 2026-03 | MCB | TRUE | high | outdoor unit PCB failure | control_board | FALSE | TRUE | Other | na | EODA18H2436 | EODA18H | 1.5 |  |  | 2026-03-25 |  | unknown | bad board at condenser | This call involved troubleshooting a condenser unit with technician John, guided by Mauricio from Eco. They discussed error codes, system monitoring, voltage issues, and the need for a surge protector and replacement parts. Mauricio provided technical guidance, warranty procedures, and recommended system protections. Recap John, a technician on the roof in Falmouth, Massachusetts, reported a heat zero error code on an Eco condenser unit and was guided through system diagnostics and error code reading using the display and BS3 button. Mauricio explained how to interpret fault codes, monitor system status, and the importance of not shutting off the unit during troubleshooting. The system was running in heat mode with low and high-pressure readings indicating potential voltage issues, confirmed by voltage measurements of approximately 215V, which is typical for a commercial system. Mauricio advised testing the compressor's ohms and suggested voltage stability as a possible cause of error codes. Mauricio recommended installing a surge protector to prevent damage to the control board due to voltage fluctuations, and explained warranty procedures for replacement boards, emphasizing the importance of capturing images of the model and serial numbers, and the surge protector for warranty claims. The conversation included discussions about the system's monitoring capabilities, the benefits of remote system management via an app, and Mauricio's upcoming training sessions and system offerings, highlighting the company's focus on advanced, monitored HVAC solutions. Tasks Mauricio will send John a part number for the replacement control board and a warranty claim number via text message. John will install a surge protector on the system when replacing the control board and send Mauricio pictures of the surge protector and the system's model and serial numbers. John will test the compressor's ohms as Mauricio instructed to further diagnose the voltage issue. Mauricio will provide John with additional technical support and training information for future system maintenance and troubleshooting. |  | EODA18H2436 | na | na | 1G832WL100ZL12900105 | MCB | EAC230904173
24834 | 2026-03-27 | 2026 | 3 | 2026-03 | Motor | TRUE | high | indoor blower motor failure | mechanical | FALSE | TRUE | Other | na | EODA18H-4860 | EODA18H | 1.5 |  | 2024-04-26 | 2026-03-27 | 700 | 1-2y | Faulty indoor blower motor | Faulty indoor blower motor |  | EODA18H-4860 | EAHATN-36 | . | 1J340WL400ZL40100076 | Blower Motor | 230904148
24863 | 2026-03-31 | 2026 | 3 | 2026-03 | MCB | TRUE | high | burnt main control board | control_board | FALSE | TRUE | Other | na | EODA18H-2436 | EODA18H | 1.5 |  |  | 2026-03-30 |  | unknown | Burnt Board | Burnt Board |  | EODA18H-2436 | . | . | 1J339WL400ZL40100037 | MCB | EAC230904173
24865 | 2026-03-31 | 2026 | 3 | 2026-03 | MCB | TRUE | high | malfunctioning control board | control_board | FALSE | TRUE | Control Board | E0 | EODA18H-4860BAA | EODA18H | 1.5 |  |  | 2025-11-10 |  | unknown | issues with condenser | Brett from Coastal Mechanical reported that a unit is locked out on e0, despite having previously installed a chip and a buck booster. They discussed the voltage readings, which were lower than normal, indicating a potential issue with the unit. Mauricio instructed Brett to check the voltage going into the unit and the main board, confirming readings of 216 volts, which is lower than the typical 240 volts. After troubleshooting, they determined that the compressor was likely functioning, but the board was not working correctly, leading Mauricio to decide to create a ticket for a replacement part. Mauricio requested Brett to take pictures of the surge protector, booster, and voltage readings, which are necessary for the warranty ticket, and to send them back for record-keeping. Tasks Mauricio will send Brett a message with the ticket number and part number for the warranty. Brett is to take pictures of the surge protector, booster, and voltage readings, and send them back to Mauricio for record-keeping. Brett is advised to call the Portland group to order the replacement part as soon as they receive the message from Mauricio. |  | EODA18H-4860BAA | EAHATN-48BAA | na | 167TXWQ500ZQ51200017 | Other | EODA18H-4860
24868 | 2026-03-31 | 2026 | 3 | 2026-03 | Leakage | TRUE | high | corroded evaporator coil leaks | refrigerant | FALSE | TRUE | Other | na | na | NA |  |  | 2023-08-04 | 2026-03-30 | 969 | >2y | Leaking Coil | Coil is extremely rusty and has leaks in a couple of U-bends |  | na | EAHATN-48 | na | na | Evaporator assembly | EAC1099000009
24874 | 2026-03-31 | 2026 | 3 | 2026-03 | Gas Furnace | TRUE | high | defective gas valve | mechanical | FALSE | TRUE | Sensor | Flame would not stay lit, replaced valve, issue resolved | MGH96M060B3A | MGH96M | 5 |  | 2024-07-17 | 2026-03-15 | 606 | 1-2y | Please credit TPG Raynham for a 17427600001389 | Contractor called to home for issue with furnace. Flame would not stay lit. Furnace was getting gas. Contractor determined the gas valve was bad. Replaced and is now up and running. Part was purchased on PO P1705040. Please credit TPG Raynham for a 17427600001389 |  |  |  | MGH96M060B3A |  | Gas valve | 17427600001389
24880 | 2026-04-01 | 2026 | 4 | 2026-04 | Leakage | TRUE | high | refrigerant leak in coil | refrigerant | FALSE | TRUE | Other | na | . | . |  |  | 2019-11-15 | 2026-03-31 | 2328 | >2y | Coil Leak | need to get more info due to out in field. HH will be calling back. Putting on hold. |  | . | EAHATN-36 | . | . | Evaporator Only | EAC1099000008
24897 | 2026-04-02 | 2026 | 4 | 2026-04 | MCB | TRUE | high | failed main control board | control_board | FALSE | TRUE | Other | . | EODA19H-2436AAA | EODA19H | 2 |  | 2025-11-11 |  |  | unknown | Not preforming | System not producing any heat |  | EODA19H-2436AAA | EAHATN-36 | . | 0EWH003523Z24A100003 | MCB | MCB
24920 | 2026-04-03 | 2026 | 4 | 2026-04 | Leakage | TRUE | high | air handler coil leak | refrigerant | FALSE | TRUE | Other | na | na | NA |  |  |  | 2026-04-02 |  | unknown | coil leak at air handler | coil leak at air handler |  | na | EAHATN-24 | na | na | Evaporator assembly | EAC1099000008
24947 | 2026-04-06 | 2026 | 4 | 2026-04 | Drain Pan | TRUE | medium | cracked drain pan | drain_water | FALSE | TRUE | Other | na | . | . |  |  | 2023-10-01 | 2026-04-06 | 918 | >2y | Cracked Drain Pan | Cracked Drain Pan |  | . | EAHATN-24 | na | . | Drain Pan 1 | EAC230701545
24967 | 2026-04-07 | 2026 | 4 | 2026-04 | MCB | TRUE | high | main control board failure | control_board | FALSE | TRUE | Other | blank display | EODA18H-2436 | EODA18H | 1.5 |  | 2021-11-15 |  |  | unknown | Blank display screen, system has surge protector | blank dispaly |  | EODA18H-2436 | . | . | 1O372WL800ZL81900354 | MCB | EAC230904165
24970 | 2026-04-08 | 2026 | 4 | 2026-04 | MCB | TRUE | high | main control board failure | control_board | FALSE | TRUE | Other | na | EODA18H-4860 | EODA18H | 1.5 |  |  |  |  | unknown | BLANK DISPLAY | BLANK DISPLAY |  | EODA18H-4860 | . | . | 1W967WM300ZM32200026 | MCB | EAC230904171
24988 | 2026-04-08 | 2026 | 4 | 2026-04 | Leakage | TRUE | high | evaporator coil leak | refrigerant | FALSE | TRUE | Other | na | EODA18H-4860 | EODA18H | 1.5 |  | 2020-08-24 | 2026-04-08 | 2053 | >2y | coil leak at air handler | coil leak at air handler . per contractor email |  | EODA18H-4860 | EAHATN-36 | na | 11649WJ4280J50800052 | Evaporator assembly | EAC1099000008
24995 | 2026-04-09 | 2026 | 4 | 2026-04 | Gas Furnace | TRUE | high | defective gas valve | mechanical | FALSE | TRUE | Sensor | FE | MGH96M060B3A | MGH96M | 5 |  | 2025-02-14 | 2025-12-23 | 312 | 31-365d | Please credit TPG for a 17427600001389 | Bad gas valve. Getting FE error code. Contractor replaced and unit is now up and running. Contacted us after the fact. needed to get customer up and running with heat. Please credit TPG for a 17427600001389 |  |  |  | MGH96M060B3A |  | None;Gas valve | 17427600001389
25000 | 2026-04-09 | 2026 | 4 | 2026-04 | Leakage | TRUE | high | leaking evaporator coil | refrigerant | FALSE | TRUE | Other | na | na | NA |  |  | 2026-04-02 | 2026-04-08 | 6 | ≤30d (infant) | new air handler with a leaking coil | James Little (Distributor, FACSCO) reported a flat coil issue with an EAHATN 36 unit purchased by a contractor. Mauricio Cordeiro (Support Representative) confirmed the issue and requested the serial number for further assistance. After verifying the serial number, they discussed sending a replacement coil to the contractor. Mauricio explained the process for handling warranty claims and obtaining credit for the part. James mentioned the contractor's name as 'Electrify my Home' and confirmed the need for pictures of the defective coil. Mauricio assured James that he would create a warranty ticket and provide a part number for ordering the replacement. The conversation ended with Mauricio promising to text the warranty ticket number and part information to James. |  | na | EAHATN-36-B | na | na | Evaporator assembly | EAC1099000008

## Fault_Type_Summary
fault_type | count | avg_days_to_failure | high_severity_pct | install_issue_pct
MCB | 672 | 726 | 93.2 | 4.2
Leakage | 500 | 901 | 93.6 | 2.4
Drain Pan | 176 | 743 | 7.4 | 5.1
E-code | 163 | 375 | 62 | 12.3
Compressor | 150 | 965 | 88.7 | 5.3
Motor | 146 | 1036 | 82.9 | 2.7
IoT | 102 | 610 | 2 | 4.9
Charge | 73 | 1166 | 19.2 | 67.1
Thermostat | 67 | 191 | 13.4 | 11.9
BAD ODU | 65 | 929 | 72.3 | 13.8
Gas Furnace | 61 | 317 | 62.3 | 14.8
TXV | 49 | 442 | 61.2 | 6.1
Sensor | 46 | 973 | 34.8 | 2.2
Noise | 40 | 301 | 10 | 5
EEV KIT | 18 | 477 | 61.1 | 0
Bad AHU | 17 | 541 | 52.9 | 5.9
Valve | 16 | 538 | 81.2 | 0
Top Cover | 16 | 887 | 43.8 | 0
EMI | 14 | 1261 | 64.3 | 14.3
APP | 11 | 0 | 0 | 9.1
E-heater | 11 | 620 | 27.3 | 0
Screen | 10 | 256 | 50 | 10
KIT | 9 | 71 | 0 | 22.2
Coil | 8 |  | 75 | 25
Blower | 5 |  | 60 | 0
Burnt | 5 | 280 | 100 | 0
Rust | 5 | 187 | 0 | 0
Transformer | 4 | 579 | 100 | 50
EEV | 2 |  | 50 | 0
Leakage-motor | 1 |  | 100 | 0

## Data_Quality
metric | value
Total tickets (after dedupe) | 7105
Duplicates removed | 2
Fault tickets | 2462
Non-fault (calls/inquiries) | 4643
Tickets with install date | 1354
Tickets with failure date | 1479
Tickets with both (lifetime) | 882
Tickets with model number | 2805
AI-tagged fault tickets | 2462
Years covered | 2024, 2025, 2026